## Technical Information
Technical Information
SMA Modbus Interface
SMA_Modbus-TI-en-22 ¦ Version 2.2
Information on this Document
This document is a supplement to the technical descriptions "SMA Modbus® interface" and "SMA Cluster Controller Modbus® interface". It contains device-specific Modbus registers for SMA inverters with Speedwire interface. The individual sheets are named by the corresponding inverter type and firmware version. In each case a sheet contains the supported Modbus registers of a device with short descriptions. For additional information, please see the technical description referenced under "Additional Information". When directly connected to a TCP/IP network or when connected to SMA Cluster Controller, the Modbus registers of a device are accessible under the Unit ID = 3.
Additional Information
Additional information is available at www.SMA-Solar.com
Document title, Document type
SMA Modbus® Interface, technical description
SMA Cluster Controller Modbus® Interface, technical description
Legal Provisions
The information contained in this document is the property of SMA Solar Technology AG. Any publication, whether in whole or in part, requires prior written approval by SMA Solar Technology AG. Internal reproduction used solely for the purpose of product evaluation or other proper use is allowed and does not require prior approval.
Trademarks
All trademarks are recognized, even if not explicitly identified as such. A lack of identification does not mean that a product or symbol is not trademarked.
Modbus® is a registered trademark of Schneider Electric and is licensed by the Modbus Organization, Inc.
SMA SOLAR TECHNOLOGY AG
Sonnenallee 1
34266 Niestetal
Deutschland
Tel. +49 561 9522-0
Fax +49 561 9522-100
www.SMA.de
E-Mail: info@SMA.de
Copyright © 2016 SMA Solar Technology AG. All rights reserved.

## SMA Device Type Enum.
SMA Device Types
Type Designation | Device Type ID | Explanation
Sunny Boy
SB 5000SE-10 | 9225 | This sheet breaks down SMA device type enumerators to type designations.
SB 3600SE-10 | 9226 | The device type enumerators are provided by the
SB 3000TL-21 | 9074 | Modbus register address 30053 in "SMA Modbus Profile".
SB 3600TL-21 | 9165
SB 4000TL-21 | 9075
SB 5000TL-21 | 9076
SB 2500TLST-21 | 9184
SB 3000TLST-21 | 9185
SB 3500TL-JP-22 | 9162
SB 4500TL-JP-22 | 9164
SB 3000TL-US-22 | 9198
SB 3800TL-US-22 | 9199
SB 4000TL-US-22 | 9200
SB 5000TL-US-22 | 9201
SB 6000TL-US-22 | 9274
SB 7000TL-US-22 | 9275
SB 7700TL-US-22 | 9293
SB1.5-1VL-40 | 9301
SB2.5-1VL-40 | 9302
SB3.0-1SP-US-40 | 9328
SB3.8-1SP-US-40 | 9329
SB5.0-1SP-US-40 | 9304
SB6.0-1SP-US-40 | 9305
SB7.0-1SP-US-40 | 9330
SB7.7-1SP-US-40 | 9306
SB3.0-1AV-40 | 9319
SB3.6-1AV-40 | 9320
SB4.0-1AV-40 | 9321
SB5.0-1AV-40 | 9322
Sunny Boy Storage
SBS2.5-1VL-40 | 9326
Sunny Tripower
STP 8000TL-10 | 9101
STP 10000TL-10 | 9067
STP 12000TL-10 | 9068
STP 15000TL-10 | 9069
STP 17000TL-10 | 9070
STP 15000TLEE-10 | 9182
STP 20000TLEE-10 | 9181
STP 10000TLEE-JP-10 | 9222
STP 12000TL-US-10 | 9194
STP 15000TL-US-10 | 9195
STP 20000TL-US-10 | 9196
STP 24000TL-US-10 | 9197
STP 30000TL-US-10 | 9310
STP 20000TLEE-JP-11 | 9271
STP 10000TLEE-JP-11 | 9272
STP 5000TL-20 | 9098
STP 6000TL-20 | 9099
STP 7000TL-20 | 9100
STP 8000TL-20 | 9103
STP 9000TL-20 | 9102
STP 10000TL-20 | 9281
STP 11000TL-20 | 9282
STP 12000TL-20 | 9283
STP 20000TL-30 | 9284
STP 25000TL-30 | 9285
STP 25000TL-JP-30 | 9311
Sunny Island
Sunny Island 3.0M | 9278
Sunny Island 4.4M | 9279
Sunny Island 6.0H | 9223
Sunny Island 8.0H | 9224

## STP nn000TL-10, PKG 2.65
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class |  | U32 | ENUM | RO | Sunny Tripower with "Speedwire data module"
30053 | Device type |  | U32 | ENUM | RO | Sunny Tripower: STP 8000TL-10, STP 10000TL-10, STP 12000TL-10, STP 15000TL-10, STP 17000TL-10
30057 | Serial number |  | U32 | RAW | RO | Speedwire data module: SWDM-10
30059 | Software package |  | U32 | FW | RO | Starting with software package: 2.65.02.R
30197 | Current event number |  | U32 | FIX0 | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action |  | U32 | ENUM | RO
30213 | Message |  | U32 | ENUM | RO
30215 | Fault correction measure |  | U32 | ENUM | RO
30217 | Grid relay/contactor |  | U32 | ENUM | RO
30219 | Derating |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30797 | Grid current phase L1 | A | U32 | FIX3 | RO
30799 | Grid current phase L2 | A | U32 | FIX3 | RO
30801 | Grid current phase L3 | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30919 | Oper.mode vol.maint.at Q on Dem., st.vol.maint.conf. |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A |  | U32 | ENUM | RO
30931 | Connection speed of SMACOM B |  | U32 | ENUM | RO
30933 | Duplex mode of SMACOM B |  | U32 | ENUM | RO
30935 | Speedwire connection status of SMACOM B |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition |  | U32 | ENUM | RW
40013 | Language of the user interface |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40157 | Automatic speedwire configureation switched on |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config. |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40244 | Reactive current droop, full dynamic grid support configuration |  | U32 | ENUM | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration |  | U32 | ENUM | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | % | S32 | FIX0 | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40260 | Characteristic curve number of the PV system control procedure P(U) |  | U32 | FIX0 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNX server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay [1] |  | U32 | ENUM | RW
40577 | Operating mode of multifunction relay [2] |  | U32 | ENUM | RW
40579 | Operating mode of multifunction relay [3] |  | U32 | ENUM | RW
40581 | Operating mode of multifunction relay [4] |  | U32 | ENUM | RW
40583 | Operating mode of multifunction relay [5] |  | U32 | ENUM | RW
40585 | Operating mode of multifunction relay [6] |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40809 | Revision status of the logic component |  | U32 | FIX0 | RO
40915 | Set active power limit | W | U32 | FIX0 | RW
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SB nn00TL-21, PKG 2.81
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Boy with "Speedwire data module"
30053 | Device type: 9074 = SB 3000TL-21 9075 = SB 4000TL-21 9076 = SB 5000TL-21 9165 = SB 3600TL-21 |  | U32 | ENUM | RO | Sunny Boy: SB 3000TL-21, SB 3600TL-21, SB 4000TL-21, SB 5000TL-21
30057 | Serial number |  | U32 | RAW | RO | Speedwire data module: SWDM-10
30059 | Software package |  | U32 | FW | RO | Starting with software package: 2.81.03.R
30197 | Current event number |  | U32 | FIX0 | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30881 | PV mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30931 | Connection speed of SMACOM B: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30933 | Duplex mode of SMACOM B: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30935 | Speedwire connection status of SMACOM B: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40029 | Operating status: 295 = MPP 1467 = Start 381 = Stop 2119 = Derating 1469 = Shut down 1392 = Fault 1480 = Waiting for utilities company 1393 = Waiting for PV voltage 443 = Constant voltage 1855 = Stand-alone operation |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40101 | Frequency monitoring lower minimum threshold | Hz | U32 | FIX2 | RW
40103 | Frequency monitoring upper maximum threshold | Hz | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 560 = EN50438 561 = EN50438-CZ 1013 = Other standard 1199 = PPDS 7501 = RD1663/661-A 7506 = VDE0126-1-1/UTE 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7517 = CEI 0-21 internal 7518 = CEI 0-21 external 7522 = NEN-EN50438 7523 = C10/11/2012 7524 = RD1699 7525 = G83/2 7526 = VFR2013 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7549 = AS4777.2_2015 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40155 | MAC address |  | STR32 | UTF8 | RO
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40183 | Phase assignment: 325 = Phase L1 327 = Phase L2 329 = Phase L3 |  | U32 | ENUM | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40260 | Characteristic curve number of the PV system control procedure P(U) |  | U32 | FIX0 | RW
40426 | Frq. monitoring upper max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40444 | Frq. monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40809 | Revision status of the logic component |  | U32 | FIX0 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41001 | Maximum achievable reactive power quadrant 1 | VAr | S32 | FIX0 | RO
41007 | Maximum achievable reactive power quadrant 4 | VAr | S32 | FIX0 | RO
41009 | Minimum achievable cos(phi) quadrant 1 |  | S32 | FIX3 | RO
41015 | Minimum achievable cos(phi) quadrant 4 |  | S32 | FIX3 | RO
41017 | Adjustment time of characteristic operating point, conf. of grid integr. char. 1 | s | U32 | FIX1 | RW
41019 | Decrease ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41021 | Increase ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41023 | Number of points to be used, conf. of grid integr. char. 1 |  | U32 | FIX0 | RW
41025 | X-axes reference, conf. of grid integration char. 1: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41027 | Y-axes reference, conf. of grid integration char. 1: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 3565 = VAr as percentage of available reactive power |  | U32 | ENUM | RW
41029 | X value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41031 | Y value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41033 | X value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41035 | Y value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41037 | X value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41039 | Y value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41041 | X value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41043 | Y value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41045 | X value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41047 | Y value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41049 | X value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41051 | Y value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41053 | X value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41055 | Y value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41057 | X value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41059 | Y value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41065 | Adjustment time of char. operating point, conf. of grid integration char. 2 | s | U32 | FIX1 | RW
41067 | Decrease ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41069 | Increase ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41071 | Number of points to be used, conf. of grid integr. char. 2 |  | U32 | FIX0 | RW
41073 | Input unit, conf. of grid integration char. 2: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41075 | Output frequency, conf. of grid integration char. 2: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 3565 = VAr as percentage of available reactive power |  | U32 | ENUM | RW
41077 | X value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41079 | Y value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41081 | X value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41083 | Y value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41085 | X value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41087 | Y value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41089 | X value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41091 | Y value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41093 | X value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41095 | Y value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41097 | X value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41099 | Y value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41101 | X value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41103 | Y value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41105 | X value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41107 | Y value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41121 | Set country standard: 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 560 = EN50438 561 = EN50438-CZ 1013 = Other standard 1199 = PPDS 7501 = RD1663/661-A 7506 = VDE0126-1-1/UTE 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7517 = CEI 0-21 internal 7518 = CEI 0-21 external 7522 = NEN-EN50438 7523 = C10/11/2012 7524 = RD1699 7525 = G83/2 7526 = VFR2013 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7549 = AS4777.2_2015 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41133 | Minimum voltage input [2] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41157 | Start delay input [2] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
41219 | Operating mode for absent reactive power control: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41221 | Timeout for absent reactive power control | s | U32 | Duration | RW
41223 | Fallback react power Q in % of WMax for absent react power ctr | % | S32 | FIX2 | RW
41225 | Operating mode for absent cos Phi spec: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41227 | Timeout for absent cos Phi spec | s | U32 | Duration | RW
41229 | Fallback cos Phi for absent cos Phi spec |  | S32 | FIX4 | RW
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SB n000TL-JP-22, PKG 2.62
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO | Sunny Boy JP version with "Speedwire data module"
30053 | Device type | U32 | ENUM |  | RO | Sunny Boy: SB 3500TL-JP-22, SB 4500TL-JP-22
30057 | Serial number | U32 | RAW |  | RO | Speedwire data module: SWDM-10
30059 | Software package | U32 | FW |  | RO | Starting with software package: 2.62.30.R
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30931 | Connection speed of SMACOM B | U32 | ENUM |  | RO
30933 | Duplex mode of SMACOM B | U32 | ENUM |  | RO
30935 | Speedwire connection status of SMACOM B | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30957 | DC current input [2] | S32 | FIX3 | A | RO
30959 | DC voltage input [2] | S32 | FIX2 | V | RO
30961 | DC power input [2] | S32 | FIX0 | W | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the central processing unit | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40101 | Frequency monitoring lower minimum threshold | U32 | FIX2 | Hz | RW
40103 | Frequency monitoring upper maximum threshold | U32 | FIX2 | Hz | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40426 | Frq. monitoring upper max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40444 | Frq. monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40789 | Communication version | U32 | REV |  | RO
40809 | Revision status of the logic component | U32 | FIX0 |  | RO
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## STP nn000TLEE-10, PKG 2.5
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO | Sunny Tripower Economic Excellence with "Speedwire data module"
30053 | Device type | U32 | ENUM |  | RO | Sunny Tripower: STP 15000TLEE-10, STP 20000TLEE-10
30057 | Serial number | U32 | RAW |  | RO | Speedwire data module: SWDM-10
30059 | Software package | U32 | FW |  | RO | Starting with software package: 2.50.87.R
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30819 | Apparent power L3 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30919 | Oper.mode vol.maint.at Q on Dem., st.vol.maint.conf. | U32 | ENUM |  | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30931 | Connection speed of SMACOM B | U32 | ENUM |  | RO
30933 | Duplex mode of SMACOM B | U32 | ENUM |  | RO
30935 | Speedwire connection status of SMACOM B | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
31159 | Current spec. reactive power Q | S32 | FIX0 | VAr | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the main processor | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40244 | Reactive current droop, full dynamic grid support configuration | U32 | ENUM |  | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration | U32 | ENUM | 0 | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | S32 | FIX0 | % | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | U32 | FIX0 | % | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40258 | PWM inversion delay, dynamic grid support configuration | U32 | FIX2 | s | RW
40260 | Characteristic curve number of the PV system control procedure P(U) | U32 | FIX0 | 0 | RW
40428 | Frequency monitoring median maximum threshold | U32 | FIX2 | Hz | RW
40430 | Frq. monitoring median max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40440 | Frequency monitoring median minimum threshold | U32 | FIX2 | Hz | RW
40442 | Frq. monitoring median min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40789 | Communication version | U32 | REV |  | RO
40809 | Revision status of the logic component | U32 | FIX0 |  | RO
40915 | Set active power limit | U32 | FIX0 | W | RW
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SB nn00TLST-21, PKG 2.80
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO | Sunny Boy with "Speedwire data module"
30053 | Device type | U32 | ENUM |  | RO | Sunny Boy: SB 2500TLST-21, SB 3000TLST-21
30057 | Serial number | U32 | RAW |  | RO | Speedwire data module: SWDM-10
30059 | Software package | U32 | FW |  | RO | Starting with software package: 2.80.22.R
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30819 | Apparent power L3 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30931 | Connection speed of SMACOM B | U32 | ENUM |  | RO
30933 | Duplex mode of SMACOM B | U32 | ENUM |  | RO
30935 | Speedwire connection status of SMACOM B | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
31159 | Current spec. reactive power Q | S32 | FIX0 | VAr | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the central processing unit | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40101 | Frequency monitoring lower minimum threshold | U32 | FIX2 | Hz | RW
40103 | Frequency monitoring upper maximum threshold | U32 | FIX2 | Hz | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40183 | Phase assignment | U32 | ENUM |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40260 | Characteristic curve number of the PV system control procedure P(U) | U32 | FIX0 | 0 | RW
40426 | Frq. monitoring upper max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40444 | Frq. monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40789 | Communication version | U32 | REV |  | RO
40809 | Revision status of the logic component | U32 | FIX0 |  | RO
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## STP nn000TL-US-10, PKG 2.82
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Tripower US version with "Speedwire data module"
30053 | Device type: 9194 = STP 12000TL-US-10 9195 = STP 15000TL-US-10 9196 = STP 20000TL-US-10 9197 = STP 24000TL-US-10 9309 = STP 27000TL-US-10 9310 = STP 30000TL-US-10 |  | U32 | ENUM | RO | Sunny Tripower: STP 12000TL-US-10, STP 15000TL-US-10, STP 20000TL-US-10, STP 24000TL-US-10 and STP 30000TL-US-10
30057 | Serial number |  | U32 | RAW | RO | Speedwire data module: SWDM-10
30059 | Software package |  | U32 | FW | RO | Starting with software package: 2.82.00.R
30197 | Current event number |  | U32 | FIX0 | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30235 | Backup mode status: 1440 = Grid mode 1441 = Separate network mode 16777213 = Information not available |  | U32 | ENUM | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30797 | Grid current phase L1 | A | U32 | FIX3 | RO
30799 | Grid current phase L2 | A | U32 | FIX3 | RO
30801 | Grid current phase L3 | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains |  | U32 | ENUM | RO
30919 | Oper.mode vol.maint.at Q on Dem., st.vol.maint.conf.: 303 = Off 2476 = As static voltage stability |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30931 | Connection speed of SMACOM B: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30933 | Duplex mode of SMACOM B: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30935 | Speedwire connection status of SMACOM B: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down |  | U32 | ENUM | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40029 | Operating status: 295 = MPP 1467 = Start 381 = Stop 2119 = Derating 1469 = Shut down 1392 = Fault 1480 = Waiting for utilities company 1393 = Waiting for PV voltage 443 = Constant voltage 1855 = Stand-alone operation |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 306 = Island mode 60 Hz 1013 = Other standard 7519 = UL1741/2010/277 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40155 |  |  | STR32 | UTF8 | RO
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40244 | Reactive current droop, full dynamic grid support configuration: 1233 = SDLWindV 1020 = Medium-Voltage Directive (Germany) |  | U32 | ENUM | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1265 = Limited dynamic grid support 1264 = Full dynamic grid support |  | U32 | ENUM | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | % | S32 | FIX0 | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40791 | Timeout for communication fault indication | s | U32 | FIX0 | RW
40809 | Revision status of the logic component |  | U32 | FIX0 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40917 | Characteristic curve number, configuration of characteristic curve mode [1] |  | U32 | FIX0 | RW
40937 | Activation of the characteristic curve, configuration of characteristic curve mode: [1] 303 = Off 308 = On |  | U32 | ENUM | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41017 | Adjustment time of characteristic operating point, conf. of grid integr. char. 1 | s | U32 | FIX1 | RW
41019 | Decrease ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41021 | Increase ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41023 | Number of points to be used, conf. of grid integr. char. 1 |  | U32 | FIX0 | RW
41025 | X-axes reference, conf. of grid integration char. 1: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41027 | Y-axes reference, conf. of grid integration char. 1: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power |  | U32 | ENUM | RW
41029 | X value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41031 | Y value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41033 | X value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41035 | Y value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41037 | X value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41039 | Y value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41041 | X value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41043 | Y value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41045 | X value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41047 | Y value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41049 | X value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41051 | Y value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41053 | X value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41055 | Y value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41057 | X value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41059 | Y value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41061 | 2nd characteristic curve number, configuration of characteristic curve mode |  | U32 | FIX0 | RW
41063 | 2nd activation of the characteristic curve, configuration of characteristic curve mode: 303 = Off 308 = On |  | U32 | ENUM | RW
41065 | Adjustment time of char. operating point, conf. of grid integration char. 2 | s | U32 | FIX1 | RW
41067 | Decrease ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41069 | Increase ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41071 | Number of points to be used, conf. of grid integr. char. 2 |  | U32 | FIX0 | RW
41073 | Input unit, conf. of grid integration char. 2: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41075 | Output frequency, conf. of grid integration char. 2: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power |  | U32 | ENUM | RW
41077 | X value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41079 | Y value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41081 | X value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41083 | Y value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41085 | X value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41087 | Y value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41089 | X value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41091 | Y value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41093 | X value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41095 | Y value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41097 | X value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41099 | Y value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41101 | X value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41103 | Y value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41105 | X value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41107 | Y value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41111 | Voltage monitoring of lower minimum threshold as RMS value | V | U32 | FIX2 | RW
41113 | Voltage monitoring of lower min.threshold as RMS value for tripping time | ms | U32 | FIX0 | RW
41115 | Voltage monitoring of upper maximum threshold as RMS value | V | U32 | FIX2 | RW
41117 | Voltage monitoring of upper max. thresh. as RMS value for tripping time | ms | U32 | FIX0 | RW
41121 | Set country standard: 306 = Island mode 60 Hz 1013 = Other standard 7519 = UL1741/2010/277 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41133 | Minimum voltage input [2] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41157 | Start delay input [2] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
41219 | Operating mode for absent reactive power control: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41221 | Timeout for absent reactive power control | s | U32 | Duration | RW
41223 | Fallback react power Q in % of WMax for absent react power ctr | % | S32 | FIX2 | RW
41225 | Operating mode for absent cos Phi spec: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41227 | Timeout for absent cos Phi spec | s | U32 | Duration | RW
41229 | Fallback cos Phi for absent cos Phi spec |  | S32 | FIX4 | RW

## SB n000TL-US-22, PKG 2.65
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Boy US version with "Speedwire data module"
30053 | Device type: 9198 = SB 3000TLUS-22 9199 = SB 3800TLUS-22 9200 = SB 4000TLUS-22 9201 = SB 5000TLUS-22 9274 = SB 6000TL-US-22 9275 = SB 7000TL-US-22 9293 = SB 7700TL-US-22 |  | U32 | ENUM | RO | Sunny Boy: SB 3000TL-US-22, SB 3800TL-US-22, SB 4000TL-US-22 and SB 5000TL-US-22
30057 | Serial number |  | U32 | RAW | RO | Sunny Boy: SB 6000TL-US-22, SB 7000TL-US-22 and SB 7700TL-US-22
30059 | Software package |  | U32 | FW | RO | Speedwire data module: SWDM-10
30197 | Current event number |  | U32 | FIX0 | RO | Starting with software package: 2.65.03.R
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30235 | Backup mode status: 1440 = Grid mode 1441 = Separate network mode 16777213 = Information not available |  | U32 | ENUM | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30789 | Grid voltage phase L1 against L2 | V | U32 | FIX2 | RO
30791 | Grid voltage phase L2 against L3 | V | U32 | FIX2 | RO
30793 | Grid voltage phase L3 against L1 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30931 | Connection speed of SMACOM B: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30933 | Duplex mode of SMACOM B: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30935 | Speedwire connection status of SMACOM B: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage 1855 = Stand-alone operation |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40029 | Operating status: 295 = MPP 1467 = Start 381 = Stop 2119 = Derating 1469 = Shut down 1392 = Fault 1480 = Waiting for utilities company 1393 = Waiting for PV voltage 443 = Constant voltage 1855 = Stand-alone operation |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40101 | Frequency monitoring lower minimum threshold | Hz | U32 | FIX2 | RW
40103 | Frequency monitoring upper maximum threshold | Hz | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 306 = Island mode 60 Hz 313 = Island mode 50 Hz 1013 = Other standard 7520 = UL1741/2010/120 7548 = HECO2015 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40155 | MAC address |  | STR32 | UTF8 | RO
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40183 | Phase assignment: 402 = Phases L1 and L2 403 = Phases L1 and L3 404 = Phases L2 and L3 |  | U32 | ENUM | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40426 | Frq. monitoring upper max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40444 | Frq. monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40809 | Revision status of the logic component |  | U32 | FIX0 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40917 | Characteristic curve number, configuration of characteristic curve mode [1] |  | U32 | FIX0 | RW
40937 | Activation of the characteristic curve, configuration of characteristic curve mode: [1] 303 = Off 308 = On |  | U32 | ENUM | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41001 | Maximum achievable reactive power quadrant 1 | VAr | S32 | FIX0 | RO
41007 | Maximum achievable reactive power quadrant 4 | VAr | S32 | FIX0 | RO
41009 | Minimum achievable cos(phi) quadrant 1 |  | S32 | FIX3 | RO
41015 | Minimum achievable cos(phi) quadrant 4 |  | S32 | FIX3 | RO
41017 | Adjustment time of characteristic operating point, conf. of grid integr. char. 1 | s | U32 | FIX1 | RW
41019 | Decrease ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41021 | Increase ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41023 | Number of points to be used, conf. of grid integr. char. 1 |  | U32 | FIX0 | RW
41025 | X-axes reference, conf. of grid integration char. 1: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41027 | Y-axes reference, conf. of grid integration char. 1: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 3565 = VAr as percentage of available reactive power |  | U32 | ENUM | RW
41029 | X value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41031 | Y value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41033 | X value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41035 | Y value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41037 | X value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41039 | Y value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41041 | X value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41043 | Y value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41045 | X value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41047 | Y value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41049 | X value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41051 | Y value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41053 | X value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41055 | Y value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41057 | X value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41059 | Y value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41061 | 2nd characteristic curve number, configuration of characteristic curve mode |  | U32 | FIX0 | RW
41063 | 2nd activation of the characteristic curve, configuration of characteristic curve mode: 303 = Off 308 = On |  | U32 | ENUM | RW
41065 | Adjustment time of char. operating point, conf. of grid integration char. 2 | s | U32 | FIX1 | RW
41067 | Decrease ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41069 | Increase ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41071 | Number of points to be used, conf. of grid integr. char. 2 |  | U32 | FIX0 | RW
41073 | Input unit, conf. of grid integration char. 2: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41075 | Output frequency, conf. of grid integration char. 2: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 3565 = VAr as percentage of available reactive power |  | U32 | ENUM | RW
41077 | X value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41079 | Y value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41081 | X value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41083 | Y value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41085 | X value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41087 | Y value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41089 | X value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41091 | Y value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41093 | X value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41095 | Y value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41097 | X value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41099 | Y value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41101 | X value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41103 | Y value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41105 | X value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41107 | Y value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41111 | Voltage monitoring of lower minimum threshold as RMS value | V | U32 | FIX2 | RW
41113 | Voltage monitoring of lower min.threshold as RMS value for tripping time | ms | U32 | FIX0 | RW
41115 | Voltage monitoring of upper maximum threshold as RMS value | V | U32 | FIX2 | RW
41117 | Voltage monitoring of upper max. thresh. as RMS value for tripping time | ms | U32 | FIX0 | RW
41121 | Set country standard: 306 = Island mode 60 Hz 313 = Island mode 50 Hz 1013 = Other standard 7520 = UL1741/2010/120 7548 = HECO2015 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41133 | Minimum voltage input [2] | V | U32 | FIX2 | RW
41143 | Critical voltage to end feed-in [1] | V | U32 | FIX2 | RW
41145 | Critical voltage to end feed-in [2] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41157 | Start delay input [2] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SI 6.0-8.0H-11, PKG 3.1
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Scale factor | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO |  | Sunny Island with "Speedwire data module Sunny Island"
30053 | Device type | U32 | ENUM |  | RO |  | Sunny Island: SI 6.0H-11 and SI 8.0H-11
30057 | Serial number | U32 | RAW |  | RO |  | Speedwire data module Sunny Island: SWDMSI-NR10
30059 | Software package | U32 | FW |  | RO |  | Starting with software package: 3.100
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO | 1
30201 | Condition | U32 | ENUM |  | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30565 | Number of generator starts | U32 | FIX0 |  | RO
30567 | Amp hours counter for battery charge | U32 | FIX0 | Ah | RO
30569 | Amp hours counter for battery discharge | U32 | FIX0 | Ah | RO
30571 | Meter reading consumption meter | U32 | FIX0 | Wh | RO
30577 | Energy consumed from grid (today) | U32 | FIX0 | Wh | RO
30579 | Energy fed into grid (today) | U32 | FIX0 | Wh | RO
30581 | Grid reference counter reading | U32 | FIX0 | Wh | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30585 | Power outage | U32 | Duration | s | RO | 1
30587 | PV generation counter reading | U32 | FIX0 | Wh | RO
30589 | Rise in self-consumption | U32 | FIX0 | Wh | RO
30591 | Rise in self-consumption today | U32 | FIX0 | Wh | RO
30593 | Energy consumed internally | U32 | FIX0 | Wh | RO
30595 | Absorbed energy | U32 | FIX0 | Wh | RO
30597 | Released energy | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30843 | Battery current | S32 | FIX3 | A | RO
30845 | Current battery state of charge | U32 | FIX0 | % | RO
30847 | Current battery capacity | U32 | FIX0 | % | RO
30849 | Battery temperature | S32 | TEMP | °C | RO | 0.1
30851 | Battery voltage | U32 | FIX2 | V | RO
30853 | Active battery charging mode | U32 | ENUM |  | RO
30855 | Current battery charging set voltage | U32 | FIX2 | V | RO
30857 | Number of battery charge throughputs | S32 | FIX0 |  | RO
30859 | Battery maint. state of charge | U32 | ENUM |  | RO
30861 | Load power | S32 | FIX0 | W | RO
30865 | Power grid reference | S32 | FIX0 | W | RO
30867 | Power grid feed-in | S32 | FIX0 | W | RO
30869 | PV power generated | S32 | FIX0 | W | RO
30871 | Current self-consumption | U32 | FIX0 | W | RO
30873 | Current rise in self-consumption | S32 | FIX0 | W | RO
30875 | Multifunction relay status | U32 | ENUM |  | RO
30877 | Power supply status | U32 | ENUM |  | RO
30879 | Reason for generator request | U32 | ENUM |  | RO
30881 | PV mains connection | U32 | ENUM |  | RO
30883 | Status of utility grid | U32 | ENUM |  | RO
30885 | Output external power connection | U32 | FIX0 | W | RO
30887 | Output external power connection phase A | U32 | FIX0 | W | RO
30889 | Output external power connection phase B | U32 | FIX0 | W | RO
30891 | Output external power connection phase C | U32 | FIX0 | W | RO
30893 | Reactive power external power connection | U32 | FIX0 | VAr | RO
30895 | Reactive power external power connection phase A | U32 | FIX0 | VAr | RO
30897 | Reactive power external power connection phase B | U32 | FIX0 | VAr | RO
30899 | Reactive power external power connection phase C | U32 | FIX0 | VAr | RO
30901 | Grid frequency of external power connection | U32 | FIX2 | Hz | RO
30903 | Voltage external power connection phase A | U32 | FIX2 | V | RO
30905 | Voltage external power connection phase B | U32 | FIX2 | V | RO
30907 | Voltage external power connection phase C | U32 | FIX2 | V | RO
30909 | Electricity external power connection phase A | S32 | FIX3 | A | RO
30911 | Electricity external power connection phase B | S32 | FIX3 | A | RO
30913 | Electricity external power connection phase C | S32 | FIX3 | A | RO
30915 | Power supply status | U32 | ENUM |  | RO
30917 | Generator status | U32 | ENUM |  | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30977 | Grid current phase L1 | S32 | FIX3 | A | RO
30979 | Grid current phase L2 | S32 | FIX3 | A | RO
30981 | Grid current phase L3 | S32 | FIX3 | A | RO
30983 | Output of photovoltaics | U32 | FIX0 | W | RO
30985 | Total current external network connection | S32 | FIX3 | A | RO
30987 | Fault battery state of charge | U32 | FIX1 | % | RO
30989 | Maximum battery current in charge direction | U32 | FIX3 | A | RO
30991 | Maximum battery current in discharge direction | U32 | FIX3 | A | RO
30993 | Charge factor: ratio of battery charge/discharge | U32 | FIX3 |  | RO
30995 | Operating time of battery statistics counter | U32 | Duration | s | RO | 0.001
30997 | Lowest measured battery temperature | S32 | TEMP | °C | RO | 0.1
30999 | Highest measured battery temperature | S32 | TEMP | °C | RO | 0.01
31001 | Max. occurred battery voltage | U32 | FIX2 | V | RO
31003 | Remaining time until full charge | U32 | Duration | s | RO | 1
31005 | Remaining time until equalization charge | U32 | Duration | s | RO | 0.1
31007 | Remaining absorption time | U32 | Duration | s | RO | 1
31009 | Lower discharge limit for private consumption range | U32 | FIX0 | % | RO
31011 | Total output current of solar charger | U32 | FIX3 | A | RO
31013 | Remaining min. operating time of generator | U32 | Duration | s | RO | 0.001
31015 | Operating status Master (Phase L1) | U32 | ENUM |  | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31053 | Operating status Slave1 (Phase L2) | U32 | ENUM |  | RO
31055 | Operating status Slave2 (Phase L3) | U32 | ENUM |  | RO
31057 | Status battery application area | U32 | ENUM |  | RO
31059 | Absorption phase active | U32 | ENUM |  | RO
31061 | Control of battery charging via communication available | U32 | ENUM |  | RO
31063 | Total energy of photovoltaics | U32 | FIX0 | kWh | RO
31065 | Total energy of photovoltaics current day | U32 | FIX0 | Wh | RO
31067 | Number of battery equalization charges | U32 | FIX0 | kWh | RO
31069 | Number of battery full charges | U32 | FIX0 |  | RO
31071 | Relative battery discharge since last full charge | U32 | FIX0 | % | RO
31073 | Relative battery discharge since last equalization charge | U32 | FIX0 | % | RO
31075 | Operating time energy count | U32 | Duration | s | RO | 1
31077 | Photovoltaic energy in solar charger [1] | U32 | FIX0 | Wh | RO
34657 | Status digital input | U32 | ENUM |  | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40031 | Rated battery capacity | U32 | FIX0 | Ah | RO
40033 | Max. battery temperature | U32 | TEMP | °C | RW | 1
40035 | Battery type | U32 | ENUM |  | RO
40037 | Rated battery voltage | U32 | FIX0 | V | RO
40039 | Battery boost charge time | U32 | Duration | min | RW | 1
40041 | Battery equalization charge time | U32 | Duration | h | RW | 1
40043 | Battery full charge time | U32 | Duration | h | RW | 1
40045 | Max. battery charging current | U32 | FIX3 | A | RW
40047 | Rated generator current | U32 | FIX3 | A | RW
40049 | Automatic generator start | U32 | ENUM |  | RW
40055 | Manual generator control | U32 | ENUM |  | RW
40057 | Generator request via power on | U32 | ENUM |  | RW
40059 | Generator shutdown load limit | U32 | FIX0 | W | RW
40061 | Generator startup load limit | U32 | FIX0 | W | RW
40063 | Firmware version of the main processor | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40071 | Grid creating generator | U32 | ENUM |  | RW
40075 | Rise in self-consumption switched on | U32 | ENUM |  | RW
40077 | Initiate device restart | U32 | FUNKTION_SEC |  | RW
40085 | Cell charge nominal voltage for boost charge | U32 | FIX2 | V | RW
40087 | Cell charge nominal voltage for full charging | U32 | FIX2 | V | RW
40089 | Cell charge nominal voltage for equalization charge | U32 | FIX2 | V | RW
40091 | Cell charge nominal voltage for float charge | U32 | FIX2 | V | RW
40093 | Voltage monitoring upper minimum threshold | U32 | FIX2 | V | RW
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40097 | Voltage monitoring hysteresis minimum threshold | U32 | FIX2 | V | RW
40099 | Voltage monitoring hysteresis maximum threshold | U32 | FIX2 | V | RW
40101 | Frequency monitoring lower minimum threshold | U32 | FIX2 | Hz | RW
40103 | Frequency monitoring upper maximum threshold | U32 | FIX2 | Hz | RW
40105 | Frequency monitoring hysteresis minimum threshold | U32 | FIX2 | Hz | RW
40107 | Frequency monitoring hysteresis maximum threshold | U32 | FIX2 | Hz | RW
40111 | Voltage monit. gener. lower minimum threshold | U32 | FIX2 | V | RW
40113 | Voltage monit. gener. upper maximum threshold | U32 | FIX2 | V | RW
40119 | Frequency monit. generator lower minimum threshold | U32 | FIX2 | Hz | RW
40121 | Frequency monit. generator without max. threshold | U32 | FIX2 | Hz | RW
40127 | Voltage monitoring generator maximum reverse power | U32 | FIX0 | W | RW
40129 | Volt. monit. gener. max. reverse power trip. time | U32 | Duration | s | RW | 1
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40137 | Acknowledge generator errors | U32 | ENUM |  | RW
40149 | Active power setpoint | S32 | FIX0 | W | WO
40151 | Eff./reac. pow. contr. via comm. | U32 | ENUM |  | WO
40153 | Reactive power setpoint | S32 | FIX0 | VAr | WO
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40187 | Battery nominal capacity | U32 | FIX0 | Wh | RO
40189 | Batt. manuf's max. charge capac. | U32 | FIX0 | W | RO
40191 | Batt. manuf's max. disch. capac. | U32 | FIX0 | W | RO
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40236 | BMS operating mode | U32 | ENUM |  | WO
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40521 | Network request via power switched on | U32 | ENUM |  | RW
40523 | Network request switch-on power limit | U32 | FIX0 | W | RW
40525 | Network request switch-off power limit | U32 | FIX0 | W | RW
40527 | Manual control of network connection | U32 | ENUM |  | RW
40529 | Network request via charge type | U32 | ENUM |  | RW
40531 | Type of AC subdistribution | U32 | ENUM |  | RO
40533 | Manual equalization charge | U32 | ENUM |  | RW
40535 | Generator request | U32 | ENUM |  | RW
40537 | Limit battery state of charge generator start in time range | U32 | FIX0 | % | RW
40539 | Limit battery state of charge gen. shutdown in time range | U32 | FIX0 | % | RW
40541 | Start time additional time range generator request | U32 | TM |  | RW
40543 | Start time range for generator request | U32 | TM |  | RW
40545 | Limit battery state of charge generator stop in add time range | U32 | FIX0 | % | RW
40547 | Limit battery state of charge generator start in add time range | U32 | FIX0 | % | RW
40549 | Time-controlled generator operation | U32 | ENUM |  | RW
40551 | Start time for time-controlled generator op. | U32 | DT |  | RW
40553 | Operating time for time-controlled generator op. | U32 | Duration | s | RW | 1
40555 | Repeat cycle of time-controlled generator op. | U32 | ENUM |  | RW
40557 | Generator request with set charge type | U32 | ENUM |  | RW
40559 | Reaction to digital input of generator request | U32 | ENUM |  | RW
40561 | Average time for generator request via power | U32 | Duration | s | RW | 1
40563 | Average operating time of generator | U32 | Duration | s | RW | 1
40565 | Average idle period of generator | U32 | Duration | s | RW | 1
40567 | Cooling down time of generator | U32 | Duration | s | RW | 1
40569 | Idle period after generator fault | U32 | Duration | s | RW | 1
40571 | Warm-up time of generator | U32 | Duration | s | RW | 1
40573 | Generator nominal frequency | U32 | FIX2 | Hz | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40587 | Slave 1: Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40599 | Slave 2: Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40611 | Repeat cycle time of relay control for timer [1] | U32 | ENUM |  | RW
40615 | Duration for which multifunction relay is activated for timer [1] | U32 | Duration | s | RW | 1
40619 | Start date of relay control for timer [1] | U32 | DT |  | RW
40623 | Time-controlled inverter operation | U32 | ENUM |  | RW
40625 | Start date for time-controlled inverter operation | U32 | DT |  | RW
40627 | Operating time for time-controlled inverter op. | U32 | Duration | s | RW | 1
40629 | Repeat cycle for time-controlled inverter op. | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40647 | Automatic updates activated | U32 | ENUM |  | RW
40649 | Time of the automatic update | U32 | TM |  | RW
40651 | Conn. point of counter on measuring interface 1 | U32 | ENUM |  | RW
40653 | Conn. point of counter on measuring interface 2 | U32 | ENUM |  | RW
40657 | Serial number of the counter on meas. interface 1 | U32 | RAW |  | RW
40659 | Serial number of the counter on meas. interface 2 | U32 | RAW |  | RW
40663 | Grid Guard version | U32 | REV |  | RO
40665 | Memory card status | U32 | ENUM |  | RO
40667 | Update version of the main processor | U32 | FW |  | RO
40669 | Start feed-in PV | U32 | TM |  | RW
40671 | Stop feed-in PV | U32 | TM |  | RW
40673 | Cut-off time until connection to external network | U32 | Duration | s | RW | 1
40675 | Automatic frequency regulation | U32 | ENUM |  | RW
40677 | Maximum current from public grid | U32 | FIX3 | A | RW
40679 | Power feedback to public grid allowed | U32 | ENUM |  | RW
40681 | Network request via battery state of charge switched on | U32 | ENUM |  | RW
40683 | Lmt battery state of charge for connection to grid | U32 | FIX0 | % | RW
40685 | Lmt battery state of charge for disconnection from grid | U32 | FIX0 | % | RW
40687 | Start time additional time range grid request | U32 | TM |  | RW
40689 | Start interval for network request | U32 | TM |  | RW
40691 | Limit battery state of charge for connect to grid in add time range | U32 | FIX0 | % | RW
40693 | Limit battery state of charge for disconnect from grid in add time range | U32 | FIX0 | % | RW
40695 | Energy saving mode switched on | U32 | ENUM |  | RW
40697 | Maximum network reverse power | U32 | FIX0 | W | RW
40699 | Maximum network reverse power tripping time | U32 | Duration | s | RW | 1
40701 | Time until change-over to energy saving mode | U32 | Duration | s | RW | 1
40703 | Maximum duration of energy saving mode | U32 | Duration | s | RW | 1
40705 | Upper state of charge for reactivating feed-in | U32 | FIX0 | % | RW
40707 | Lower state of charge for locking feed-in | U32 | FIX0 | % | RW
40709 | Start time of battery protection mode level | U32 | TM |  | RW
40711 | End time of battery protection mode level | U32 | TM |  | RW
40713 | Battery state of charge for protection mode | U32 | FIX1 | % | RW
40715 | Battery switch-on limit after overtemp. shutdown | S32 | TEMP | °C | RW | 0.1
40717 | Output resistance of battery connection | U32 | FIX3 | Ohms | RW
40719 | Lower lmt deep disch. protect area prior shutdown | U32 | FIX0 | % | RW
40721 | Minimum width of deep discharge protection area | U32 | FIX0 | % | RW
40723 | Minimum width of backup power area | U32 | FIX0 | % | RW
40725 | Area width for conserving battery state of charge | U32 | FIX0 | % | RW
40727 | Minimum width of own consumption area | U32 | FIX0 | % | RW
40729 | Most productive month for battery usage range | U32 | ENUM |  | RW
40731 | Season operation active | U32 | ENUM |  | RW
40733 | Voltage setpoint with deactivated battery mgmt | U32 | FIX2 | V | RW
40735 | Cycle time full charge | U32 | Duration | s | RW | 1
40737 | Cycle time equalization charge | U32 | Duration | s | RW | 1
40739 | Battery temperature compensation | S32 | FIX3 | V/°C | RW
40741 | Automatic equalization charge | U32 | ENUM |  | RW
40743 | Type of additional DC sources | U32 | ENUM |  | RW
40745 | Limitation type of generator current | U32 | ENUM |  | RW
40747 | Sensitivity of generator failure detection | U32 | ENUM |  | RW
40749 | Status digital input | U32 | ENUM |  | RO
40751 | Inverter nominal voltage | U32 | FIX0 | V | RW
40753 | Inverter nominal frequency | U32 | FIX0 | Hz | RW
40755 | Maximum AC battery charge current | U32 | FIX3 | A | RW
40757 | Lmt value battery state of charge for start load shedding 1 | U32 | FIX0 | % | RW
40759 | Lmt value battery state of charge for stop load shedding 1 | U32 | FIX0 | % | RW
40761 | Start time additional time range load shedding 1 | U32 | TM |  | RW
40763 | Time load shedding 1 | U32 | TM |  | RW
40765 | Limit battery state of charge for start load shedding 1 in add time range | U32 | FIX0 | % | RW
40767 | Limit battery state of charge for stop load shedding 1 in add time range | U32 | FIX0 | % | RW
40769 | Lmt value battery state of charge for start load shedding 2 | U32 | FIX0 | % | RW
40771 | Lmt value battery state of charge for stop load shedding 2 | U32 | FIX0 | % | RW
40773 | Start time additional time range load shedding 2 | U32 | TM |  | RW
40775 | Time load shedding 2 | U32 | TM |  | RW
40777 | Limit battery state of charge for start load shedding 2 in add time range | U32 | FIX0 | % | RW
40779 | Limit battery state of charge for stop load shedding 2 in add time range | U32 | FIX0 | % | RW
40781 | Temp lmt for multifunct. relay with batt comp fan | S32 | TEMP | °C | RW | 0.1
40783 | Serial no. Slave1 (Phase L2) | U32 | RAW |  | RO
40785 | Serial no. Slave2 (Phase L3) | U32 | RAW |  | RO
40787 | Cluster behaviour when a device fails | U32 | ENUM |  | RW
40789 | Communication version | U32 | REV |  | RO
40791 | Timeout for communication fault indication | U32 | FIX0 | s | RW | 1
40795 | Max. battery charge capac. | U32 | FIX0 | W | WO
40799 | Max. battery discharge capac. | U32 | FIX0 | W | WO
40805 | Energy saving mode | U32 | ENUM |  | WO
40811 | Update version of the logic component | U32 | FW |  | RO
40819 | Firmware version of protocol converter | U32 | FW |  | RO
40821 | Hardware version of protocol converter | U32 | HW |  | RO
40827 | Serial number of the protocol converter | U32 | RAW |  | RO
40829 | SUSyID of protocol converter | U32 | FIX0 |  | RO
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SI 3.0-4.4M-11, PKG 3.2
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Scale factor | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO |  | Sunny Island with "Speedwire data module Sunny Island"
30053 | Device type | U32 | ENUM |  | RO |  | Sunny Island: SI 3.0M-11 and SI 4.4M-11
30057 | Serial number | U32 | RAW |  | RO |  | Speedwire data module Sunny Island: SWDMSI-NR10
30059 | Software package | U32 | FW |  | RO |  | Starting with software package: 3.200
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO | 1
30201 | Condition | U32 | ENUM |  | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30565 | Number of generator starts | U32 | FIX0 |  | RO
30567 | Amp hours counter for battery charge | U32 | FIX0 | Ah | RO
30569 | Amp hours counter for battery discharge | U32 | FIX0 | Ah | RO
30571 | Meter reading consumption meter | U32 | FIX0 | Wh | RO
30577 | Energy consumed from grid (today) | U32 | FIX0 | Wh | RO
30579 | Energy fed into grid (today) | U32 | FIX0 | Wh | RO
30581 | Grid reference counter reading | U32 | FIX0 | Wh | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30585 | Power outage | U32 | Duration | s | RO | 1
30587 | PV generation counter reading | U32 | FIX0 | Wh | RO
30589 | Rise in self-consumption | U32 | FIX0 | Wh | RO
30591 | Rise in self-consumption today | U32 | FIX0 | Wh | RO
30593 | Energy consumed internally | U32 | FIX0 | Wh | RO
30595 | Absorbed energy | U32 | FIX0 | Wh | RO
30597 | Released energy | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30843 | Battery current | S32 | FIX3 | A | RO
30845 | Current battery state of charge | U32 | FIX0 | % | RO
30847 | Current battery capacity | U32 | FIX0 | % | RO
30849 | Battery temperature | S32 | TEMP | °C | RO | 0.1
30851 | Battery voltage | U32 | FIX2 | V | RO
30853 | Active battery charging mode | U32 | ENUM |  | RO
30855 | Current battery charging set voltage | U32 | FIX2 | V | RO
30857 | Number of battery charge throughputs | S32 | FIX0 |  | RO
30859 | Battery maint. state of charge | U32 | ENUM |  | RO
30861 | Load power | S32 | FIX0 | W | RO
30865 | Power grid reference | S32 | FIX0 | W | RO
30867 | Power grid feed-in | S32 | FIX0 | W | RO
30869 | PV power generated | S32 | FIX0 | W | RO
30871 | Current self-consumption | U32 | FIX0 | W | RO
30873 | Current rise in self-consumption | S32 | FIX0 | W | RO
30875 | Multifunction relay status | U32 | ENUM |  | RO
30877 | Power supply status | U32 | ENUM |  | RO
30879 | Reason for generator request | U32 | ENUM |  | RO
30881 | PV mains connection | U32 | ENUM |  | RO
30883 | Status of utility grid | U32 | ENUM |  | RO
30885 | Output external power connection | U32 | FIX0 | W | RO
30887 | Output external power connection phase A | U32 | FIX0 | W | RO
30889 | Output external power connection phase B | U32 | FIX0 | W | RO
30891 | Output external power connection phase C | U32 | FIX0 | W | RO
30893 | Reactive power external power connection | U32 | FIX0 | VAr | RO
30895 | Reactive power external power connection phase A | U32 | FIX0 | VAr | RO
30897 | Reactive power external power connection phase B | U32 | FIX0 | VAr | RO
30899 | Reactive power external power connection phase C | U32 | FIX0 | VAr | RO
30901 | Grid frequency of external power connection | U32 | FIX2 | Hz | RO
30903 | Voltage external power connection phase A | U32 | FIX2 | V | RO
30905 | Voltage external power connection phase B | U32 | FIX2 | V | RO
30907 | Voltage external power connection phase C | U32 | FIX2 | V | RO
30909 | Electricity external power connection phase A | S32 | FIX3 | A | RO
30911 | Electricity external power connection phase B | S32 | FIX3 | A | RO
30913 | Electricity external power connection phase C | S32 | FIX3 | A | RO
30915 | Power supply status | U32 | ENUM |  | RO
30917 | Generator status | U32 | ENUM |  | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30977 | Grid current phase L1 | S32 | FIX3 | A | RO
30979 | Grid current phase L2 | S32 | FIX3 | A | RO
30981 | Grid current phase L3 | S32 | FIX3 | A | RO
30983 | Output of photovoltaics | U32 | FIX0 | W | RO
30985 | Total current external network connection | S32 | FIX3 | A | RO
30987 | Fault battery state of charge | U32 | FIX1 | % | RO
30989 | Maximum battery current in charge direction | U32 | FIX3 | A | RO
30991 | Maximum battery current in discharge direction | U32 | FIX3 | A | RO
30993 | Charge factor: ratio of battery charge/discharge | U32 | FIX3 |  | RO
30995 | Operating time of battery statistics counter | U32 | Duration | s | RO | 0.001
30997 | Lowest measured battery temperature | S32 | TEMP | °C | RO | 0.1
30999 | Highest measured battery temperature | S32 | TEMP | °C | RO | 0.01
31001 | Max. occurred battery voltage | U32 | FIX2 | V | RO
31003 | Remaining time until full charge | U32 | Duration | s | RO | 1
31005 | Remaining time until equalization charge | U32 | Duration | s | RO | 0.1
31007 | Remaining absorption time | U32 | Duration | s | RO | 1
31009 | Lower discharge limit for private consumption range | U32 | FIX0 | % | RO
31011 | Total output current of solar charger | U32 | FIX3 | A | RO
31013 | Remaining min. operating time of generator | U32 | Duration | s | RO | 0.001
31015 | Operating status Master (Phase L1) | U32 | ENUM |  | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31053 | Operating status Slave1 (Phase L2) | U32 | ENUM |  | RO
31055 | Operating status Slave2 (Phase L3) | U32 | ENUM |  | RO
31057 | Status battery application area | U32 | ENUM |  | RO
31059 | Absorption phase active | U32 | ENUM |  | RO
31061 | Control of battery charging via communication available | U32 | ENUM |  | RO
31063 | Total energy of photovoltaics | U32 | FIX0 | kWh | RO
31065 | Total energy of photovoltaics current day | U32 | FIX0 | Wh | RO
31067 | Number of battery equalization charges | U32 | FIX0 | kWh | RO
31069 | Number of battery full charges | U32 | FIX0 |  | RO
31071 | Relative battery discharge since last full charge | U32 | FIX0 | % | RO
31073 | Relative battery discharge since last equalization charge | U32 | FIX0 | % | RO
31075 | Operating time energy count | U32 | Duration | s | RO | 1
31077 | Photovoltaic energy in solar charger [1] | U32 | FIX0 | Wh | RO
34657 | Status digital input | U32 | ENUM |  | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40031 | Rated battery capacity | U32 | FIX0 | Ah | RO
40033 | Max. battery temperature | U32 | TEMP | °C | RW | 1
40035 | Battery type | U32 | ENUM |  | RO
40037 | Rated battery voltage | U32 | FIX0 | V | RO
40039 | Battery boost charge time | U32 | Duration | min | RW | 1
40041 | Battery equalization charge time | U32 | Duration | h | RW | 1
40043 | Battery full charge time | U32 | Duration | h | RW | 1
40045 | Max. battery charging current | U32 | FIX3 | A | RW
40047 | Rated generator current | U32 | FIX3 | A | RW
40049 | Automatic generator start | U32 | ENUM |  | RW
40055 | Manual generator control | U32 | ENUM |  | RW
40057 | Generator request via power on | U32 | ENUM |  | RW
40059 | Generator shutdown load limit | U32 | FIX0 | W | RW
40061 | Generator startup load limit | U32 | FIX0 | W | RW
40063 | Firmware version of the main processor | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40071 | Grid creating generator | U32 | ENUM |  | RW
40075 | Rise in self-consumption switched on | U32 | ENUM |  | RW
40077 | Initiate device restart | U32 | FUNKTION_SEC |  | RW
40085 | Cell charge nominal voltage for boost charge | U32 | FIX2 | V | RW
40087 | Cell charge nominal voltage for full charging | U32 | FIX2 | V | RW
40089 | Cell charge nominal voltage for equalization charge | U32 | FIX2 | V | RW
40091 | Cell charge nominal voltage for float charge | U32 | FIX2 | V | RW
40093 | Voltage monitoring upper minimum threshold | U32 | FIX2 | V | RW
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40097 | Voltage monitoring hysteresis minimum threshold | U32 | FIX2 | V | RW
40099 | Voltage monitoring hysteresis maximum threshold | U32 | FIX2 | V | RW
40101 | Frequency monitoring lower minimum threshold | U32 | FIX2 | Hz | RW
40103 | Frequency monitoring upper maximum threshold | U32 | FIX2 | Hz | RW
40105 | Frequency monitoring hysteresis minimum threshold | U32 | FIX2 | Hz | RW
40107 | Frequency monitoring hysteresis maximum threshold | U32 | FIX2 | Hz | RW
40111 | Voltage monit. gener. lower minimum threshold | U32 | FIX2 | V | RW
40113 | Voltage monit. gener. upper maximum threshold | U32 | FIX2 | V | RW
40119 | Frequency monit. generator lower minimum threshold | U32 | FIX2 | Hz | RW
40121 | Frequency monit. generator without max. threshold | U32 | FIX2 | Hz | RW
40127 | Voltage monitoring generator maximum reverse power | U32 | FIX0 | W | RW
40129 | Volt. monit. gener. max. reverse power trip. time | U32 | Duration | s | RW | 1
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40137 | Acknowledge generator errors | U32 | ENUM |  | RW
40149 | Active power setpoint | S32 | FIX0 | W | WO
40151 | Eff./reac. pow. contr. via comm. | U32 | ENUM |  | WO
40153 | Reactive power setpoint | S32 | FIX0 | VAr | WO
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40187 | Battery nominal capacity | U32 | FIX0 | Wh | RO
40189 | Batt. manuf's max. charge capac. | U32 | FIX0 | W | RO
40191 | Batt. manuf's max. disch. capac. | U32 | FIX0 | W | RO
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40236 | BMS operating mode | U32 | ENUM |  | WO
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40521 | Network request via power switched on | U32 | ENUM |  | RW
40523 | Network request switch-on power limit | U32 | FIX0 | W | RW
40525 | Network request switch-off power limit | U32 | FIX0 | W | RW
40527 | Manual control of network connection | U32 | ENUM |  | RW
40529 | Network request via charge type | U32 | ENUM |  | RW
40531 | Type of AC subdistribution | U32 | ENUM |  | RO
40533 | Manual equalization charge | U32 | ENUM |  | RW
40535 | Generator request | U32 | ENUM |  | RW
40537 | Limit battery state of charge generator start in time range | U32 | FIX0 | % | RW
40539 | Limit battery state of charge gen. shutdown in time range | U32 | FIX0 | % | RW
40541 | Start time additional time range generator request | U32 | TM |  | RW
40543 | Start time range for generator request | U32 | TM |  | RW
40545 | Limit battery state of charge generator stop in add time range | U32 | FIX0 | % | RW
40547 | Limit battery state of charge generator start in add time range | U32 | FIX0 | % | RW
40549 | Time-controlled generator operation | U32 | ENUM |  | RW
40551 | Start time for time-controlled generator op. | U32 | DT |  | RW
40553 | Operating time for time-controlled generator op. | U32 | Duration | s | RW | 1
40555 | Repeat cycle of time-controlled generator op. | U32 | ENUM |  | RW
40557 | Generator request with set charge type | U32 | ENUM |  | RW
40559 | Reaction to digital input of generator request | U32 | ENUM |  | RW
40561 | Average time for generator request via power | U32 | Duration | s | RW | 1
40563 | Average operating time of generator | U32 | Duration | s | RW | 1
40565 | Average idle period of generator | U32 | Duration | s | RW | 1
40567 | Cooling down time of generator | U32 | Duration | s | RW | 1
40569 | Idle period after generator fault | U32 | Duration | s | RW | 1
40571 | Warm-up time of generator | U32 | Duration | s | RW | 1
40573 | Generator nominal frequency | U32 | FIX2 | Hz | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40587 | Slave 1: Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40599 | Slave 2: Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40611 | Repeat cycle time of relay control for timer [1] | U32 | ENUM |  | RW
40615 | Duration for which multifunction relay is activated for timer [1] | U32 | Duration | s | RW | 1
40619 | Start date of relay control for timer [1] | U32 | DT |  | RW
40623 | Time-controlled inverter operation | U32 | ENUM |  | RW
40625 | Start date for time-controlled inverter operation | U32 | DT |  | RW
40627 | Operating time for time-controlled inverter op. | U32 | Duration | s | RW | 1
40629 | Repeat cycle for time-controlled inverter op. | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40647 | Automatic updates activated | U32 | ENUM |  | RW
40649 | Time of the automatic update | U32 | TM |  | RW
40651 | Conn. point of counter on measuring interface 1 | U32 | ENUM |  | RW
40653 | Conn. point of counter on measuring interface 2 | U32 | ENUM |  | RW
40657 | Serial number of the counter on meas. interface 1 | U32 | RAW |  | RW
40659 | Serial number of the counter on meas. interface 2 | U32 | RAW |  | RW
40663 | Grid Guard version | U32 | REV |  | RO
40665 | Memory card status | U32 | ENUM |  | RO
40667 | Update version of the main processor | U32 | FW |  | RO
40669 | Start feed-in PV | U32 | TM |  | RW
40671 | Stop feed-in PV | U32 | TM |  | RW
40673 | Cut-off time until connection to external network | U32 | Duration | s | RW | 1
40675 | Automatic frequency regulation | U32 | ENUM |  | RW
40677 | Maximum current from public grid | U32 | FIX3 | A | RW
40679 | Power feedback to public grid allowed | U32 | ENUM |  | RW
40681 | Network request via battery state of charge switched on | U32 | ENUM |  | RW
40683 | Lmt battery state of charge for connection to grid | U32 | FIX0 | % | RW
40685 | Lmt battery state of charge for disconnection from grid | U32 | FIX0 | % | RW
40687 | Start time additional time range grid request | U32 | TM |  | RW
40689 | Start interval for network request | U32 | TM |  | RW
40691 | Limit battery state of charge for connect to grid in add time range | U32 | FIX0 | % | RW
40693 | Limit battery state of charge for disconnect from grid in add time range | U32 | FIX0 | % | RW
40695 | Energy saving mode switched on | U32 | ENUM |  | RW
40697 | Maximum network reverse power | U32 | FIX0 | W | RW
40699 | Maximum network reverse power tripping time | U32 | Duration | s | RW | 1
40701 | Time until change-over to energy saving mode | U32 | Duration | s | RW | 1
40703 | Maximum duration of energy saving mode | U32 | Duration | s | RW | 1
40705 | Upper state of charge for reactivating feed-in | U32 | FIX0 | % | RW
40707 | Lower state of charge for locking feed-in | U32 | FIX0 | % | RW
40709 | Start time of battery protection mode level | U32 | TM |  | RW
40711 | End time of battery protection mode level | U32 | TM |  | RW
40713 | Battery state of charge for protection mode | U32 | FIX1 | % | RW
40715 | Battery switch-on limit after overtemp. shutdown | S32 | TEMP | °C | RW | 0.1
40717 | Output resistance of battery connection | U32 | FIX3 | Ohms | RW
40719 | Lower lmt deep disch. protect area prior shutdown | U32 | FIX0 | % | RW
40721 | Minimum width of deep discharge protection area | U32 | FIX0 | % | RW
40723 | Minimum width of backup power area | U32 | FIX0 | % | RW
40725 | Area width for conserving battery state of charge | U32 | FIX0 | % | RW
40727 | Minimum width of own consumption area | U32 | FIX0 | % | RW
40729 | Most productive month for battery usage range | U32 | ENUM |  | RW
40731 | Season operation active | U32 | ENUM |  | RW
40733 | Voltage setpoint with deactivated battery mgmt | U32 | FIX2 | V | RW
40735 | Cycle time full charge | U32 | Duration | s | RW | 1
40737 | Cycle time equalization charge | U32 | Duration | s | RW | 1
40739 | Battery temperature compensation | S32 | FIX3 | V/°C | RW
40741 | Automatic equalization charge | U32 | ENUM |  | RW
40743 | Type of additional DC sources | U32 | ENUM |  | RW
40745 | Limitation type of generator current | U32 | ENUM |  | RW
40747 | Sensitivity of generator failure detection | U32 | ENUM |  | RW
40749 | Status digital input | U32 | ENUM |  | RO
40751 | Inverter nominal voltage | U32 | FIX0 | V | RW
40753 | Inverter nominal frequency | U32 | FIX0 | Hz | RW
40755 | Maximum AC battery charge current | U32 | FIX3 | A | RW
40757 | Lmt value battery state of charge for start load shedding 1 | U32 | FIX0 | % | RW
40759 | Lmt value battery state of charge for stop load shedding 1 | U32 | FIX0 | % | RW
40761 | Start time additional time range load shedding 1 | U32 | TM |  | RW
40763 | Time load shedding 1 | U32 | TM |  | RW
40765 | Limit battery state of charge for start load shedding 1 in add time range | U32 | FIX0 | % | RW
40767 | Limit battery state of charge for stop load shedding 1 in add time range | U32 | FIX0 | % | RW
40769 | Lmt value battery state of charge for start load shedding 2 | U32 | FIX0 | % | RW
40771 | Lmt value battery state of charge for stop load shedding 2 | U32 | FIX0 | % | RW
40773 | Start time additional time range load shedding 2 | U32 | TM |  | RW
40775 | Time load shedding 2 | U32 | TM |  | RW
40777 | Limit battery state of charge for start load shedding 2 in add time range | U32 | FIX0 | % | RW
40779 | Limit battery state of charge for stop load shedding 2 in add time range | U32 | FIX0 | % | RW
40781 | Temp lmt for multifunct. relay with batt comp fan | S32 | TEMP | °C | RW | 0.1
40783 | Serial no. Slave1 (Phase L2) | U32 | RAW |  | RO
40785 | Serial no. Slave2 (Phase L3) | U32 | RAW |  | RO
40787 | Cluster behaviour when a device fails | U32 | ENUM |  | RW
40789 | Communication version | U32 | REV |  | RO
40791 | Timeout for communication fault indication | U32 | FIX0 | s | RW | 1
40795 | Max. battery charge capac. | U32 | FIX0 | W | WO
40799 | Max. battery discharge capac. | U32 | FIX0 | W | WO
40805 | Energy saving mode | U32 | ENUM |  | WO
40811 | Update version of the logic component | U32 | FW |  | RO
40819 | Firmware version of protocol converter | U32 | FW |  | RO
40821 | Hardware version of protocol converter | U32 | HW |  | RO
40827 | Serial number of the protocol converter | U32 | RAW |  | RO
40829 | SUSyID of protocol converter | U32 | FIX0 |  | RO
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SB 3600-5000SE-10, PKG 2.4
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO | Sunny Boy Smart Energy
30053 | Device type | U32 | ENUM |  | RO | Sunny Boy Smart Energy: SB 3600SE-10 and SB 5000SE-10
30057 | Serial number | U32 | RAW |  | RO | Starting with software package: 2.40.70.R
30059 | Software package | U32 | FW |  | RO
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30581 | Grid reference counter reading | U32 | FIX0 | Wh | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30819 | Apparent power L3 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30843 | Battery current | S32 | FIX3 | A | RO
30845 | Current battery state of charge | U32 | FIX0 | % | RO
30847 | Current battery capacity | U32 | FIX0 | % | RO
30851 | Battery voltage | U32 | FIX2 | V | RO
30855 | Current battery charging set voltage | U32 | FIX2 | V | RO
30865 | Power grid reference | S32 | FIX0 | W | RO
30867 | Power grid feed-in | S32 | FIX0 | W | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30955 | Battery oper. status | U32 | ENUM | 0 | RO
30957 | DC current input [2] | S32 | FIX3 | A | RO
30959 | DC voltage input [2] | S32 | FIX2 | V | RO
30961 | DC power input [2] | S32 | FIX0 | W | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
31159 | Current spec. reactive power Q | S32 | FIX0 | VAr | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the main processor | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40073 | Lower discharge limit for rise in self-consumption | U32 | FIX0 | % | RW
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40101 | Frequency monitoring lower minimum threshold | U32 | FIX2 | Hz | RW
40103 | Frequency monitoring upper maximum threshold | U32 | FIX2 | Hz | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40183 | Phase assignment | U32 | ENUM |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40187 | Battery nominal capacity | U32 | FIX0 | Wh | RO
40189 | Batt. manuf's max. charge capac. | U32 | FIX0 | W | RO
40191 | Batt. manuf's max. disch. capac. | U32 | FIX0 | W | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40236 | BMS operating mode | U32 | ENUM | 0 | WO
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40260 | Characteristic curve number of the PV system control procedure P(U) | U32 | FIX0 | 0 | RW
40426 | Frq. monitoring upper max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40444 | Frq. monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40647 | Automatic updates activated | U32 | ENUM |  | RW
40789 | Communication version | U32 | REV |  | RO
40793 | Min. battery charge capac. | U32 | FIX0 | W | WO
40795 | Max. battery charge capac. | U32 | FIX0 | W | WO
40797 | Min. battery discharge capac. | U32 | FIX0 | W | WO
40799 | Max. battery discharge capac. | U32 | FIX0 | W | WO
40801 | Mains exch. capac. target value | S32 | FIX0 | W | WO
40809 | Revision status of the logic component | U32 | FIX0 |  | RO
40915 | Set active power limit | U32 | FIX0 | W | RW
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## STP nn000TLEE-JP10_11, PKG 2.63
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO | Sunny Tripower Economic Excellence with "Speedwire data module"
30053 | Device type | U32 | ENUM |  | RO | Sunny Tripower JP: STP 10000TLEE-JP-10, STP 10000TLEE-JP-11, STP 20000TLEE-JP-11
30057 | Serial number | U32 | RAW |  | RO | Speedwire data module: SWDM-10
30059 | Software package | U32 | FW |  | RO | Starting with software package: 2.63.01.R
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30251 | Restart block status | U32 | ENUM |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30789 | Grid voltage phase L1 against L2 | U32 | FIX2 | V | RO
30791 | Grid voltage phase L2 against L3 | U32 | FIX2 | V | RO
30793 | Grid voltage phase L3 against L1 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30819 | Apparent power L3 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30931 | Connection speed of SMACOM B | U32 | ENUM |  | RO
30933 | Duplex mode of SMACOM B | U32 | ENUM |  | RO
30935 | Speedwire connection status of SMACOM B | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the central processing unit | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40244 | Reactive current droop, full dynamic grid support configuration | U32 | ENUM |  | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration | U32 | ENUM | 0 | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | S32 | FIX0 | % | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | U32 | FIX0 | % | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40258 | PWM inversion delay, dynamic grid support configuration | U32 | FIX2 | s | RW
40428 | Frequency monitoring median maximum threshold | U32 | FIX2 | Hz | RW
40430 | Frq. monitoring median max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40440 | Frequency monitoring median minimum threshold | U32 | FIX2 | Hz | RW
40442 | Frq. monitoring median min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40789 | Communication version | U32 | REV |  | RO
40791 | Time-out for communication fault indication | U32 | FIX0 | s | RW
40809 | Revision status of the logic component | U32 | FIX0 |  | RO
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## STP nn000TL-30, PKG 2.80
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class | U32 | ENUM |  | RO | Sunny Tripower with "Speedwire data module"
30053 | Device type | U32 | ENUM |  | RO | Sunny Tripower: STP 20000TL-30, STP 25000TL-30
30057 | Serial number | U32 | RAW |  | RO | Speedwire data module: SWDM-10
30059 | Software package | U32 | FW |  | RO | Starting with software package: 2.80.06.R
30197 | Current event number | U32 | FIX0 |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30797 | Grid current phase L1 | U32 | FIX3 | A | RO
30799 | Grid current phase L2 | U32 | FIX3 | A | RO
30801 | Grid current phase L3 | U32 | FIX3 | A | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30819 | Apparent power L3 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30931 | Connection speed of SMACOM B | U32 | ENUM |  | RO
30933 | Duplex mode of SMACOM B | U32 | ENUM |  | RO
30935 | Speedwire connection status of SMACOM B | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30957 | DC current input [2] | S32 | FIX3 | A | RO
30959 | DC voltage input [2] | S32 | FIX2 | V | RO
30961 | DC power input [2] | S32 | FIX0 | W | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
31159 | Current spec. reactive power Q | S32 | FIX0 | VAr | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl 1041 = Capacitive 1042 = Inductive |  | U32 | ENUM | WO
40063 | Firmware version of the central processing unit | U32 | FW |  | RO
40065 | Firmware version of the logic component | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40244 | Reactive current droop, full dynamic grid support configuration | U32 | ENUM |  | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration | U32 | ENUM | 0 | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | S32 | FIX0 | % | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | U32 | FIX0 | % | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40258 | PWM inversion delay, dynamic grid support configuration | U32 | FIX2 | s | RW
40260 | Characteristic curve number of the PV system control procedure P(U) | U32 | FIX0 | 0 | RW
40428 | Frequency monitoring median maximum threshold | U32 | FIX2 | Hz | RW
40430 | Frq. monitoring median max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40440 | Frequency monitoring median minimum threshold | U32 | FIX2 | Hz | RW
40442 | Frq. monitoring median min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40575 | Operating mode of multifunction relay [1] | U32 | ENUM |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40789 | Communication version | U32 | REV |  | RO
40809 | Revision status of the logic component | U32 | FIX0 |  | RO
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW

## SBn.n-1VL-40, PKG 2.05
SMA Modbus Profile
Modbus register address | Short description | Unit | Format | Type | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Boy
30053 | Device type: 9301 = Sunny Boy 1.5 9302 = Sunny Boy 2.5 |  | U32 | ENUM | RO | Sunny Boy: SB1.5-1VL-40 and SB2.5-1VL-40
30057 | Serial number |  | U32 | RAW | RO | Starting with software package: 2.02.11.R
30059 | Software package |  | U32 | FW | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 1705 = Derating due to frequency 3520 = Derating due to voltage 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30581 | Grid reference counter reading | Wh | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30789 | Grid voltage phase L1 against L2 | V | U32 | FIX2 | RO
30791 | Grid voltage phase L2 against L3 | V | U32 | FIX2 | RO
30793 | Grid voltage phase L3 against L1 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30865 | Power grid reference | W | S32 | FIX0 | RO
30867 | Power grid feed-in | W | S32 | FIX0 | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains 16777213 = Information not available |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 1720 = 10 Mbit/s 1721 = 100 Mbit/s 3581 = No connection speed set |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 1726 = Half duplex 1727 = Full duplex 3582 = No duplex mode set |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31221 | EEI displacement power factor |  | S32 | FIX3 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40003 | Time zone: 9499 = (UTC-AUTO) Automatic via SMA protocol |  | U32 | ENUM | RW
40005 | Standard/Daylight saving time conversion on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 798 = Polski 801 = ภาษาไทย |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down: 381 = Stop 1467 = Start 1749 = Full stop |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40063 | Firmware version of the main processor |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 438 = VDE0126-1-1 7510 = VDE-AR-N4105 7517 = CEI 0-21 internal 7523 = C10/11/2012 7525 = G83/2 7527 = VFR2014 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7535 = WorstCase 7536 = Default 7539 = RD1699/413 7549 = AS4777.2_2015 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40183 | Phase assignment: 325 = Phase L1 327 = Phase L2 329 = Phase L3 |  | U32 | ENUM | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1264 = Full dynamic grid support 1265 = Limited dynamic grid support |  | U32 | ENUM | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40262 | No. of charac. pt.s to be used [1] |  | U32 | FIX0 | RW
40264 | No. of charac. pt.s to be used [2] |  | U32 | FIX0 | RW
40266 | No. of charac. pt.s to be used [3] |  | U32 | FIX0 | RW
40282 | X values charact. curve 1 [1] |  | S32 | FIX3 | RW
40284 | X values charact. curve 1 [2] |  | S32 | FIX3 | RW
40286 | X values charact. curve 1 [3] |  | S32 | FIX3 | RW
40288 | X values charact. curve 1 [4] |  | S32 | FIX3 | RW
40290 | X values charact. curve 1 [5] |  | S32 | FIX3 | RW
40292 | X values charact. curve 1 [6] |  | S32 | FIX3 | RW
40294 | X values charact. curve 1 [7] |  | S32 | FIX3 | RW
40296 | X values charact. curve 1 [8] |  | S32 | FIX3 | RW
40306 | Y values charact. curve 1 [1] |  | S32 | FIX3 | RW
40308 | Y values charact. curve 1 [2] |  | S32 | FIX3 | RW
40310 | Y values charact. curve 1 [3] |  | S32 | FIX3 | RW
40312 | Y values charact. curve 1 [4] |  | S32 | FIX3 | RW
40314 | Y values charact. curve 1 [5] |  | S32 | FIX3 | RW
40316 | Y values charact. curve 1 [6] |  | S32 | FIX3 | RW
40318 | Y values charact. curve 1 [7] |  | S32 | FIX3 | RW
40320 | Y values charact. curve 1 [8] |  | S32 | FIX3 | RW
40330 | X values charact. curve 2 [1] |  | S32 | FIX3 | RW
40332 | X values charact. curve 2 [2] |  | S32 | FIX3 | RW
40334 | X values charact. curve 2 [3] |  | S32 | FIX3 | RW
40336 | X values charact. curve 2 [4] |  | S32 | FIX3 | RW
40338 | X values charact. curve 2 [5] |  | S32 | FIX3 | RW
40340 | X values charact. curve 2 [6] |  | S32 | FIX3 | RW
40342 | X values charact. curve 2 [7] |  | S32 | FIX3 | RW
40344 | X values charact. curve 2 [8] |  | S32 | FIX3 | RW
40354 | Y values charact. curve 2 [1] |  | S32 | FIX3 | RW
40356 | Y values charact. curve 2 [2] |  | S32 | FIX3 | RW
40358 | Y values charact. curve 2 [3] |  | S32 | FIX3 | RW
40360 | Y values charact. curve 2 [4] |  | S32 | FIX3 | RW
40362 | Y values charact. curve 2 [5] |  | S32 | FIX3 | RW
40364 | Y values charact. curve 2 [6] |  | S32 | FIX3 | RW
40366 | Y values charact. curve 2 [7] |  | S32 | FIX3 | RW
40368 | Y values charact. curve 2 [8] |  | S32 | FIX3 | RW
40378 | X values charact. curve 3 [1] |  | S32 | FIX3 | RW
40380 | X values charact. curve 3 [2] |  | S32 | FIX3 | RW
40382 | X values charact. curve 3 [3] |  | S32 | FIX3 | RW
40384 | X values charact. curve 3 [4] |  | S32 | FIX3 | RW
40386 | X values charact. curve 3 [5] |  | S32 | FIX3 | RW
40388 | X values charact. curve 3 [6] |  | S32 | FIX3 | RW
40390 | X values charact. curve 3 [7] |  | S32 | FIX3 | RW
40392 | X values charact. curve 3 [8] |  | S32 | FIX3 | RW
40402 | Y values charact. curve 3 [1] |  | S32 | FIX3 | RW
40404 | Y values charact. curve 3 [2] |  | S32 | FIX3 | RW
40406 | Y values charact. curve 3 [3] |  | S32 | FIX3 | RW
40408 | Y values charact. curve 3 [4] |  | S32 | FIX3 | RW
40410 | Y values charact. curve 3 [5] |  | S32 | FIX3 | RW
40412 | Y values charact. curve 3 [6] |  | S32 | FIX3 | RW
40414 | Y values charact. curve 3 [7] |  | S32 | FIX3 | RW
40416 | Y values charact. curve 3 [8] |  | S32 | FIX3 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40480 | Nominal current of all phases | A | U32 | FIX3 | RO
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40791 | Timeout for communication fault indication | s | U32 | FIX0 | RW
40855 | Down ramp f. charac. act. pt. [1] | % | U32 | FIX1 | RW
40857 | Down ramp f. charac. act. pt. [2] | % | U32 | FIX1 | RW
40859 | Down ramp f. charac. act. pt. [3] | % | U32 | FIX1 | RW
40875 | Up ramp f. charac. act. pt. [1] | % | U32 | FIX1 | RW
40877 | Up ramp f. charac. act. pt. [2] | % | U32 | FIX1 | RW
40879 | Up ramp f. charac. act. pt. [3] | % | U32 | FIX1 | RW
40895 | Adj. time for charac. act. pt. [1] | s | U32 | FIX1 | RW
40897 | Adj. time for charac. act. pt. [2] | s | U32 | FIX1 | RW
40899 | Adj. time for charac. act. pt. [3] | s | U32 | FIX1 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40917 | Characteristic curve number, configuration of characteristic curve mode [1] |  | U32 | FIX0 | RW
40919 | Characteristic curve number, configuration of characteristic curve mode [2] |  | U32 | FIX0 | RW
40921 | Characteristic curve number, configuration of characteristic curve mode [3] |  | U32 | FIX0 | RW
40937 | Activation of the characteristic curve, configuration of characteristic curve mode: [1] 303 = Off 308 = On |  | U32 | ENUM | RW
40939 | Activation of the characteristic curve, configuration of characteristic curve mode: [2] 303 = Off 308 = On |  | U32 | ENUM | RW
40941 | Activation of the characteristic curve, configuration of characteristic curve mode: [3] 303 = Off 308 = On |  | U32 | ENUM | RW
40957 | X-axis ref. characteristic: [1] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40959 | X-axis ref. characteristic: [2] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40961 | X-axis ref. characteristic: [3] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40977 | Y-axis ref. characteristic: [1] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) 3678 = Max. power draw in % based on Pmax |  | U32 | ENUM | RW
40979 | Y-axis ref. characteristic: [2] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) 3678 = Max. power draw in % based on Pmax |  | U32 | ENUM | RW
40981 | Y-axis ref. characteristic: [3] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) 3678 = Max. power draw in % based on Pmax |  | U32 | ENUM | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41111 | Voltage monitoring of lower minimum threshold as RMS value | V | U32 | FIX2 | RW
41113 | Voltage monitoring of lower min.threshold as RMS value for tripping time | ms | U32 | FIX0 | RW
41115 | Voltage monitoring of upper maximum threshold as RMS value | V | U32 | FIX2 | RW
41117 | Voltage monitoring of upper max. thresh. as RMS value for tripping time | ms | U32 | FIX0 | RW
41121 | Set country standard: 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 438 = VDE0126-1-1 7510 = VDE-AR-N4105 7517 = CEI 0-21 internal 7523 = C10/11/2012 7525 = G83/2 7527 = VFR2014 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7535 = WorstCase 7536 = Default 7539 = RD1699/413 7549 = AS4777.2_2015 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
41199 | Set active power limit at grid connection point | % | U32 | FIX0 | RW
41203 | Nominal PV system power | W | U32 | FIX0 | RW
41217 | Set active power limit at grid connection point | W | U32 | FIX0 | RW
41219 | Operating mode for absent reactive power control: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41221 | Timeout for absent reactive power control | s | U32 | Duration | RW
41223 | Fallback react power Q in % of WMax for absent react power ctr | % | S32 | FIX2 | RW
41225 | Operating mode for absent cos Phi spec: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41227 | Timeout for absent cos Phi spec | s | U32 | Duration | RW
41229 | Fallback cos Phi for absent cos Phi spec |  | S32 | FIX4 | RW
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW

## STP nn000TL-JP-30, PKG 1.00
SMA Modbus Profile
Modbus register address | Short description / Enumerators | Unit | Format | Type | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Tripower with "Speedwire data module" Sunny Tripower JP: STP 25000TL-JP-30
30053 | Device type: 9311 = STP 25000TL-JP-30 |  | U32 | ENUM | RO | Speedwire data module: SWDM-10 Starting with software package: 1.00.12.R
30057 | Serial number |  | U32 | RAW | RO
30059 | Software package |  | U32 | FW | RO
30197 | Current event number |  | U32 | FIX0 | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30251 | Restart block status: 87 = Grid frequency disturbance 302 = ------- 2386 = Overvoltage 2387 = Undervoltage 2390 = Passive island detection 3167 = Active island detection 16777213 = Information not available |  | U32 | ENUM | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30789 | Grid voltage phase L1 against L2 | V | U32 | FIX2 | RO
30791 | Grid voltage phase L2 against L3 | V | U32 | FIX2 | RO
30793 | Grid voltage phase L3 against L1 | V | U32 | FIX2 | RO
30797 | Grid current phase L1 | A | U32 | FIX3 | RO
30799 | Grid current phase L2 | A | U32 | FIX3 | RO
30801 | Grid current phase L3 | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30919 | Oper.mode vol.maint.at Q on Dem., st.vol.maint.conf.: 303 = Off 2476 = As static voltage stability |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30931 | Connection speed of SMACOM B: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30933 | Duplex mode of SMACOM B: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30935 | Speedwire connection status of SMACOM B: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | WO
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | WO
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | WO
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | WO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 7508 = 7509 = 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40155 | MAC address |  | STR32 | UTF8 | RO
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40244 | Reactive current droop, full dynamic grid support configuration: 1233 = SDLWindV 1020 = Medium-Voltage Directive (Germany) |  | U32 | ENUM | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1265 = Limited dynamic grid support 1264 = Full dynamic grid support |  | U32 | ENUM | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | % | S32 | FIX0 | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNX server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40809 | Revision status of the logic component |  | U32 | FIX0 | RO
40915 | Set active power limit | W | U32 | FIX0 | RW
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW

## SBn.n-1SP-US-40, PKG 2.02
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Boy
30053 | Device type: 9328 = Sunny Boy 3.0 9329 = Sunny Boy 3.8 9304 = Sunny Boy 5.0 9305 = Sunny Boy 6.0 9330 = Sunny Boy 7.0 9306 = Sunny Boy 7.7 |  | U32 | ENUM | RO | Sunny Boy: SB3.0-1SP-US-40, SB3.8-1SP-US-40, SB5.0-1SP-US-40, SB6.0-1SP-US-40, SB7.0-1SP-US-40 and SB7.7-1SP-US-40
30057 | Serial number |  | U32 | RAW | RO | Starting with software package: 2.02.09.R
30059 | Software package |  | U32 | FW | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 1705 = Derating due to frequency 3520 = Derating due to voltage 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30235 | Backup mode status: 1440 = Grid mode 1441 = Separate network mode 16777213 = Information not available |  | U32 | ENUM | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30789 | Grid voltage phase L1 against L2 | V | U32 | FIX2 | RO
30791 | Grid voltage phase L2 against L3 | V | U32 | FIX2 | RO
30793 | Grid voltage phase L3 against L1 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30823 | Excitation type of cosPhi: 1041 = Overexcited 1042 = Underexcited 16777213 = Information not available |  | U32 | ENUM | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30875 | Multifunction relay status: 303 = Off 308 = On |  | U32 | ENUM | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains 16777213 = Information not available |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30931 | Connection speed of SMACOM B: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30933 | Duplex mode of SMACOM B: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30935 | Speedwire connection status of SMACOM B: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30963 | DC current input [3] | A | S32 | FIX3 | RO
30965 | DC voltage input [3] | V | S32 | FIX2 | RO
30967 | DC power input [3] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31221 | EEI displacement power factor |  | S32 | FIX3 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
31797 | DC current input [3] | A | S32 | FIX3 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
34609 | Ambient temperature | °C | S32 | TEMP | RO
34611 | Highest measured ambient temperature | °C | S32 | TEMP | RO
34615 | Wind speed | m/s | U32 | FIX2 | RO
34621 | Module temperature | °C | S32 | TEMP | RO
34623 | Insolation on external sensor | W/m² | U32 | FIX0 | RO
34625 | Ambient temperature | °F | S32 | TEMP | RO
34627 | Ambient temperature | K | S32 | TEMP | RO
34629 | Module temperature | °F | S32 | TEMP | RO
34631 | Module temperature | K | S32 | TEMP | RO
34633 | Wind speed | km/h | U32 | FIX2 | RO
34635 | Wind speed | mph | U32 | FIX2 | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40003 | Time zone: 9500 = (UTC+04:30) Kabul 9501 = (UTC-09:00) Alaska 9502 = (UTC+03:00) Kuwait, Riyardh 9503 = (UTC+04:00) Abu Dhabi, Muskat 9504 = (UTC+03:00) Baghdad 9505 = (UTC-04:00) Atlantic (Canada) 9506 = (UTC+09:30) Darwin 9507 = (UTC+10:00) Canberra, Melbourne, Sydney 9508 = (UTC+04:00) Baku 9509 = (UTC-01:00) Azores 9510 = (UTC-06:00) Saskatchewan 9511 = (UTC-01:00) Cape Verde Islands 9512 = (UTC+04:00) Yerevan 9513 = (UTC+09:30) Adelaide 9515 = (UTC+06:00) Astana, Dhaka 9516 = (UTC-04:00) Manaus 9517 = (UTC+01:00) Belgrade, Bratislava, Budapest, Ljubljana, Prague 9518 = (UTC+01:00) Sarajevo, Skopje, Warsaw, Zagreb 9519 = (UTC+11:00) Magadan, Solomon Islands, New Caledonia 9520 = (UTC-06:00) Central America 9522 = (UTC+08:00) Peking, Chongqing, Hongkong, Urumchi 9523 = (UTC-12:00) (Western) International Date Line 9524 = (UTC+03:00) Nairobi 9525 = (UTC+10:00) Brisbane 9528 = (UTC-05:00) New York, Miami, Atlanta, Detroit, Toronto 9530 = (UTC+05:00) Jekaterinburg 9531 = (UTC+12:00) Fidschi, Marshall Islands 9532 = (UTC+02:00) Helsinki, Kiev, Riga, Sofia, Tallin, Wilna 9533 = (UTC+04:00) Tiflis 9534 = (UTC) Dublin, Edinburgh, Lisbon, London 9535 = (UTC-03:00) Greenland 9536 = (UTC) Monrovia, Reykjavík 9537 = (UTC+02:00) Athens, Bucharest, Istanbul 9538 = (UTC-10:00) Hawaii 9539 = (UTC+05:30) Chennai, Kolkata, Mumbai, New Delhi 9541 = (UTC+02:00) Jerusalem 9542 = (UTC+02:00) Amman 9543 = (UTC+09:00) Seoul 9544 = (UTC+08:00) Kuala Lumpur, Singapore 9545 = (UTC-02:00) Central Atlantic 9546 = (UTC+02:00) Beirut 9547 = (UTC-07:00) Denver, Salt Lake City, Calgary 9549 = (UTC+06:30) Yangon (Rangoon) 9550 = (UTC+06:00) Novosibirsk 9551 = (UTC+02:00) Windhoek 9552 = (UTC+05:45) Katmandu 9553 = (UTC+12:00) Auckland, Wellington 9554 = (UTC-03:30) Newfoundland 9555 = (UTC+08:00) Irkutsk 9556 = (UTC+07:00) Krasnoyarsk 9557 = (UTC-04:00) Santiago - old 9558 = (UTC-08:00) Pacific (USA, Canada) 9559 = (UTC-08:00) Tijuana, Baja California (Mexico) 9560 = (UTC+01:00) Brussels, Copenhagen, Madrid, Paris 9561 = (UTC+03:00) Moskow, St. Petersburg, Volgograd 9562 = (UTC-03:00) Buenos Aires, Santiago 9563 = (UTC-05:00) Bogotá, Lima, Quito 9564 = (UTC-04:30) Caracas 9565 = (UTC-11:00) Midway Islands, Samoa 9566 = (UTC+07:00) Bangkok, Hanoi, Jakarta 9567 = (UTC+02:00) Harare, Pretoria 9568 = (UTC+05:30) Sri Jayawardenepura 9569 = (UTC+08:00) Taipeh 9570 = (UTC+10:00) Hobart 9571 = (UTC+09:00) Osaka, Sapporo, Tokyo 9572 = (UTC+13:00) Nuku'alofa 9573 = (UTC-05:00) Indiana (East) 9574 = (UTC-07:00) Arizona 9575 = (UTC+10:00) Vladivostok, Magadan 9576 = (UTC+08:00) Perth 9577 = (UTC+01:00) West.Centr.Africa 9578 = (UTC+01:00) Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna 9579 = (UTC+05:00) Islamabad, Karatschi 9580 = (UTC+10:00) Guam, Port Moresby 9581 = (UTC+09:00) Yakutsk 9582 = (UTC+04:00) Caucasian Standard Time 9583 = (UTC-06:00) Chicago, Dallas, Kansas City, Winnipeg 9584 = (UTC-06:00) Guadalajara, Mexico City, Monterrey - new 9586 = (UTC+04:00) Port Louis 9587 = (UTC-07:00) Chihuahua, La Paz, Mazatlan - new 9588 = (UTC-03:00) Montevideo 9589 = (UTC+05:00) Taschkent 9591 = (UTC-04:00) Georgetown, La Paz, San Juan 9592 = (UTC+08:00) Ulan-Bator 9593 = (UTC-03:00) Cayenne 9594 = (UTC-04:00) Asuncion 9595 = (UTC+12:00) Petropavlovsk-Kamtschatski 9596 = (UTC+03:00) Minsk |  | U32 | ENUM | RW
40005 | Standard/Daylight saving time conversion on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage 1855 = Stand-alone operation |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down: 381 = Stop 1467 = Start 1749 = Full stop |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40029 | Operating status: 295 = MPP 381 = Stop 443 = Constant voltage 1392 = Fault 1393 = Waiting for PV voltage 1467 = Start 1469 = Shut down 1480 = Waiting for utilities company 1855 = Stand-alone operation 2119 = Derating 16777213 = Information not available |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40077 | Initiate device restart: 1146 = Execute |  | U32 | FUNKTION_SEC | RW
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40101 | Frequency monitoring lower minimum threshold | Hz | U32 | FIX2 | RW
40103 | Frequency monitoring upper maximum threshold | Hz | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 306 = Island mode 60 Hz 313 = Island mode 50 Hz 7520 = UL1741/2010/120 7521 = UL1741/2010/240 7535 = WorstCase 7536 = Default 7541 = UL1741/2010/208 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40155 |  |  | STR32 | UTF8 | RO
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40183 | Phase assignment: 402 = Phases L1 and L2 403 = Phases L1 and L3 404 = Phases L2 and L3 |  | U32 | ENUM | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1264 = Full dynamic grid support 1265 = Limited dynamic grid support |  | U32 | ENUM | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40262 | No. of charac. pt.s to be used [1] |  | U32 | FIX0 | RW
40264 | No. of charac. pt.s to be used [2] |  | U32 | FIX0 | RW
40266 | No. of charac. pt.s to be used [3] |  | U32 | FIX0 | RW
40282 | X values charact. curve 1 [1] |  | S32 | FIX3 | RW
40284 | X values charact. curve 1 [2] |  | S32 | FIX3 | RW
40286 | X values charact. curve 1 [3] |  | S32 | FIX3 | RW
40288 | X values charact. curve 1 [4] |  | S32 | FIX3 | RW
40290 | X values charact. curve 1 [5] |  | S32 | FIX3 | RW
40292 | X values charact. curve 1 [6] |  | S32 | FIX3 | RW
40294 | X values charact. curve 1 [7] |  | S32 | FIX3 | RW
40296 | X values charact. curve 1 [8] |  | S32 | FIX3 | RW
40306 | Y values charact. curve 1 [1] |  | S32 | FIX3 | RW
40308 | Y values charact. curve 1 [2] |  | S32 | FIX3 | RW
40310 | Y values charact. curve 1 [3] |  | S32 | FIX3 | RW
40312 | Y values charact. curve 1 [4] |  | S32 | FIX3 | RW
40314 | Y values charact. curve 1 [5] |  | S32 | FIX3 | RW
40316 | Y values charact. curve 1 [6] |  | S32 | FIX3 | RW
40318 | Y values charact. curve 1 [7] |  | S32 | FIX3 | RW
40320 | Y values charact. curve 1 [8] |  | S32 | FIX3 | RW
40330 | X values charact. curve 2 [1] |  | S32 | FIX3 | RW
40332 | X values charact. curve 2 [2] |  | S32 | FIX3 | RW
40334 | X values charact. curve 2 [3] |  | S32 | FIX3 | RW
40336 | X values charact. curve 2 [4] |  | S32 | FIX3 | RW
40338 | X values charact. curve 2 [5] |  | S32 | FIX3 | RW
40340 | X values charact. curve 2 [6] |  | S32 | FIX3 | RW
40342 | X values charact. curve 2 [7] |  | S32 | FIX3 | RW
40344 | X values charact. curve 2 [8] |  | S32 | FIX3 | RW
40354 | Y values charact. curve 2 [1] |  | S32 | FIX3 | RW
40356 | Y values charact. curve 2 [2] |  | S32 | FIX3 | RW
40358 | Y values charact. curve 2 [3] |  | S32 | FIX3 | RW
40360 | Y values charact. curve 2 [4] |  | S32 | FIX3 | RW
40362 | Y values charact. curve 2 [5] |  | S32 | FIX3 | RW
40364 | Y values charact. curve 2 [6] |  | S32 | FIX3 | RW
40366 | Y values charact. curve 2 [7] |  | S32 | FIX3 | RW
40368 | Y values charact. curve 2 [8] |  | S32 | FIX3 | RW
40378 | X values charact. curve 3 [1] |  | S32 | FIX3 | RW
40380 | X values charact. curve 3 [2] |  | S32 | FIX3 | RW
40382 | X values charact. curve 3 [3] |  | S32 | FIX3 | RW
40384 | X values charact. curve 3 [4] |  | S32 | FIX3 | RW
40386 | X values charact. curve 3 [5] |  | S32 | FIX3 | RW
40388 | X values charact. curve 3 [6] |  | S32 | FIX3 | RW
40390 | X values charact. curve 3 [7] |  | S32 | FIX3 | RW
40392 | X values charact. curve 3 [8] |  | S32 | FIX3 | RW
40402 | Y values charact. curve 3 [1] |  | S32 | FIX3 | RW
40404 | Y values charact. curve 3 [2] |  | S32 | FIX3 | RW
40406 | Y values charact. curve 3 [3] |  | S32 | FIX3 | RW
40408 | Y values charact. curve 3 [4] |  | S32 | FIX3 | RW
40410 | Y values charact. curve 3 [5] |  | S32 | FIX3 | RW
40412 | Y values charact. curve 3 [6] |  | S32 | FIX3 | RW
40414 | Y values charact. curve 3 [7] |  | S32 | FIX3 | RW
40416 | Y values charact. curve 3 [8] |  | S32 | FIX3 | RW
40426 | Frq. monitoring upper max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40444 | Frq. monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40480 | Nominal current of all phases | A | U32 | FIX3 | RO
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40647 | Automatic updates activated: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40789 | Communication version |  | U32 | REV | RO
40791 | Timeout for communication fault indication | s | U32 | FIX0 | RW
40855 | Down ramp f. charac. act. pt. [1] | % | U32 | FIX1 | RW
40857 | Down ramp f. charac. act. pt. [2] | % | U32 | FIX1 | RW
40859 | Down ramp f. charac. act. pt. [3] | % | U32 | FIX1 | RW
40875 | Up ramp f. charac. act. pt. [1] | % | U32 | FIX1 | RW
40877 | Up ramp f. charac. act. pt. [2] | % | U32 | FIX1 | RW
40879 | Up ramp f. charac. act. pt. [3] | % | U32 | FIX1 | RW
40895 | Adj. time for charac. act. pt. [1] | s | U32 | FIX1 | RW
40897 | Adj. time for charac. act. pt. [2] | s | U32 | FIX1 | RW
40899 | Adj. time for charac. act. pt. [3] | s | U32 | FIX1 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40917 | Characteristic curve number, configuration of characteristic curve mode [1] |  | U32 | FIX0 | RW
40919 | Characteristic curve number, configuration of characteristic curve mode [2] |  | U32 | FIX0 | RW
40921 | Characteristic curve number, configuration of characteristic curve mode [3] |  | U32 | FIX0 | RW
40937 | Activation of the characteristic curve, configuration of characteristic curve mode: [1] 303 = Off 308 = On |  | U32 | ENUM | RW
40939 | Activation of the characteristic curve, configuration of characteristic curve mode: [2] 303 = Off 308 = On |  | U32 | ENUM | RW
40941 | Activation of the characteristic curve, configuration of characteristic curve mode: [3] 303 = Off 308 = On |  | U32 | ENUM | RW
40957 | X-axis ref. characteristic: [1] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40959 | X-axis ref. characteristic: [2] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40961 | X-axis ref. characteristic: [3] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40977 | Y-axis ref. characteristic: [1] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) |  | U32 | ENUM | RW
40979 | Y-axis ref. characteristic: [2] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) |  | U32 | ENUM | RW
40981 | Y-axis ref. characteristic: [3] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) |  | U32 | ENUM | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41001 | Maximum achievable reactive power quadrant 1 | VAr | S32 | FIX0 | RO
41007 | Maximum achievable reactive power quadrant 4 | VAr | S32 | FIX0 | RO
41009 | Minimum achievable cos(phi) quadrant 1 |  | S32 | FIX3 | RO
41015 | Minimum achievable cos(phi) quadrant 4 |  | S32 | FIX3 | RO
41111 | Voltage monitoring of lower minimum threshold as RMS value | V | U32 | FIX2 | RW
41113 | Voltage monitoring of lower min.threshold as RMS value for tripping time | ms | U32 | FIX0 | RW
41115 | Voltage monitoring of upper maximum threshold as RMS value | V | U32 | FIX2 | RW
41117 | Voltage monitoring of upper max. thresh. as RMS value for tripping time | ms | U32 | FIX0 | RW
41121 | Set country standard: 306 = Island mode 60 Hz 313 = Island mode 50 Hz 7520 = UL1741/2010/120 7521 = UL1741/2010/240 7535 = WorstCase 7536 = Default 7541 = UL1741/2010/208 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41133 | Minimum voltage input [2] | V | U32 | FIX2 | RW
41135 | Minimum voltage input [3] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41157 | Start delay input [2] | s | U32 | FIX0 | RW
41159 | Start delay input [3] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
41199 | Set active power limit at grid connection point | % | U32 | FIX0 | RW
41201 | Active power gradient in feeding operation | % | U32 | FIX0 | RW
41203 | Nominal PV system power | W | U32 | FIX0 | RW
41217 | Set active power limit at grid connection point | W | U32 | FIX0 | RW
41219 | Operating mode for absent reactive power control: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41221 | Timeout for absent reactive power control | s | U32 | Duration | RW
41223 | Fallback react power Q in % of WMax for absent react power ctr | % | S32 | FIX2 | RW
41225 | Operating mode for absent cos Phi spec: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41227 | Timeout for absent cos Phi spec | s | U32 | Duration | RW
41229 | Fallback cos Phi for absent cos Phi spec |  | S32 | FIX4 | RW
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW

## SBS2.5-1VL-40, PKG 2.04
SMA Modbus Profile
Modbus register address | Short description | Unit | Format | Type | Access | Supported hardware and firmware:
30051 | Device class: 8007 = Battery Inverter |  | U32 | ENUM | RO | Sunny Boy Storage
30053 | Device type: 9326 = Sunny Boy Storage 2.5 |  | U32 | ENUM | RO | Sunny Boy Storage: SBS2.5-1VL-40
30057 | Serial number |  | U32 | RAW | RO | Starting with software package: 2.04.08.R
30059 | Software package |  | U32 | FW | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 1705 = Derating due to frequency 3520 = Derating due to voltage 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30235 | Backup mode status: 1440 = Grid mode 1441 = Separate network mode 16777213 = Information not available |  | U32 | ENUM | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30581 | Grid reference counter reading | Wh | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30789 | Grid voltage phase L1 against L2 | V | U32 | FIX2 | RO
30791 | Grid voltage phase L2 against L3 | V | U32 | FIX2 | RO
30793 | Grid voltage phase L3 against L1 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30843 | Battery current | A | S32 | FIX3 | RO
30845 | Current battery state of charge | % | U32 | FIX0 | RO
30847 | Current battery capacity | % | U32 | FIX0 | RO
30849 | Battery temperature | °C | S32 | TEMP | RO
30851 | Battery voltage | V | U32 | FIX2 | RO
30855 | Current battery charging set voltage | V | U32 | FIX2 | RO
30865 | Power grid reference | W | S32 | FIX0 | RO
30867 | Power grid feed-in | W | S32 | FIX0 | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains 16777213 = Information not available |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 1720 = 10 Mbit/s 1721 = 100 Mbit/s 3581 = No connection speed set |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 1726 = Half duplex 1727 = Full duplex 3582 = No duplex mode set |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30955 | Battery oper. status: 303 = Off 2291 = Battery standby 2292 = Charge battery 2293 = Discharge battery 16777213 = Information not available |  | U32 | ENUM | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31009 | Lower discharge limit for private consumption range | % | U32 | FIX0 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31057 | Status battery application area: 2614 = Own consumption area 2615 = State of charge conservation area 2616 = Backup power area 2617 = Deep discharge protection area 2618 = Deep discharge area |  | U32 | ENUM | RO
31061 | Control of battery charging via communication available : 1129 = Yes 1130 = No |  | U32 | ENUM | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31221 | EEI displacement power factor |  | S32 | FIX3 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31253 | Netzspannung Phase L1 | V | U32 | FIX2 | RO
31255 | Netzspannung Phase L2 | V | U32 | FIX2 | RO
31257 | Netzspannung Phase L3 | V | U32 | FIX2 | RO
31259 | Power grid feeding L1 | W | U32 | FIX0 | RO
31261 | Power grid feeding L2 | W | U32 | FIX0 | RO
31263 | Power grid feeding L3 | W | U32 | FIX0 | RO
31265 | Power grid reference phase L1 | W | U32 | FIX0 | RO
31267 | Power grid reference phase L2 | W | U32 | FIX0 | RO
31269 | Power grid reference phase L3 | W | U32 | FIX0 | RO
31271 | Reactive power grid feeding phase L1 | VAr | S32 | FIX0 | RO
31273 | Reactive power grid feeding phase L2 | VAr | S32 | FIX0 | RO
31275 | Reactive power grid feeding phase L3 | VAr | S32 | FIX0 | RO
31277 | Reactive power grid feeding | VAr | S32 | FIX0 | RO
31377 | Battery manufacturer: 2340 = LG Chem 8605 = Tesla 16777213 = Information not available |  | U32 | ENUM | RO
31379 | BMS type: 27 = Special setting 8607 = Daily-Powerwall-6.4kWh 8610 = RESU-10.0 16777213 = Information not available |  | U32 | ENUM | RO
31381 | BMS serial number |  | STR32 | UTF8 | RO
31389 | BMS firmware version |  | U32 | FW | RO
31391 | Battery status: 35 = Fault 303 = Off 307 = Ok 455 = Warning 16777213 = Information not available |  | U32 | ENUM | RO
31393 | Present battery charge | W | U32 | FIX0 | RO
31395 | Present battery discharge | W | U32 | FIX0 | RO
31397 | Battery charge | Wh | U64 | FIX0 | RO
31401 | Battery discharge | Wh | U64 | FIX0 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
34659 | Operating status: 71 = Interference of device 388 = Operation status 898 = heating 899 = cooling 1295 = Standby 16777213 = Information not available |  | U32 | ENUM | RO
34661 | Charge of current battery | Wh | U64 | FIX0 | RO
34665 | Battery discharge of current battery | Wh | U64 | FIX0 | RO
34669 | Control of battery charging via communication available : 1129 = Yes 1130 = No |  | U32 | ENUM | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40003 | Time zone: 9500 = (UTC+04:30) Kabul 9501 = (UTC-09:00) Alaska 9502 = (UTC+03:00) Kuwait, Riyardh 9503 = (UTC+04:00) Abu Dhabi, Muskat 9504 = (UTC+03:00) Baghdad 9505 = (UTC-04:00) Atlantic (Canada) 9506 = (UTC+09:30) Darwin 9507 = (UTC+10:00) Canberra, Melbourne, Sydney 9508 = (UTC+04:00) Baku 9509 = (UTC-01:00) Azores 9510 = (UTC-06:00) Saskatchewan 9511 = (UTC-01:00) Cape Verde Islands 9512 = (UTC+04:00) Yerevan 9513 = (UTC+09:30) Adelaide 9515 = (UTC+06:00) Astana, Dhaka 9516 = (UTC-04:00) Manaus 9517 = (UTC+01:00) Belgrade, Bratislava, Budapest, Ljubljana, Prague 9518 = (UTC+01:00) Sarajevo, Skopje, Warsaw, Zagreb 9519 = (UTC+11:00) Magadan, Solomon Islands, New Caledonia 9520 = (UTC-06:00) Central America 9522 = (UTC+08:00) Peking, Chongqing, Hongkong, Urumchi 9523 = (UTC-12:00) (Western) International Date Line 9524 = (UTC+03:00) Nairobi 9525 = (UTC+10:00) Brisbane 9528 = (UTC-05:00) New York, Miami, Atlanta, Detroit, Toronto 9530 = (UTC+05:00) Jekaterinburg 9531 = (UTC+12:00) Fidschi, Marshall Islands 9532 = (UTC+02:00) Helsinki, Kiev, Riga, Sofia, Tallin, Wilna 9533 = (UTC+04:00) Tiflis 9534 = (UTC) Dublin, Edinburgh, Lisbon, London 9535 = (UTC-03:00) Greenland 9536 = (UTC) Monrovia, Reykjavík 9537 = (UTC+02:00) Athens, Bucharest, Istanbul 9538 = (UTC-10:00) Hawaii 9539 = (UTC+05:30) Chennai, Kolkata, Mumbai, New Delhi 9541 = (UTC+02:00) Jerusalem 9542 = (UTC+02:00) Amman 9543 = (UTC+09:00) Seoul 9544 = (UTC+08:00) Kuala Lumpur, Singapore 9545 = (UTC-02:00) Central Atlantic 9546 = (UTC+02:00) Beirut 9547 = (UTC-07:00) Denver, Salt Lake City, Calgary 9549 = (UTC+06:30) Yangon (Rangoon) 9550 = (UTC+06:00) Novosibirsk 9551 = (UTC+02:00) Windhoek 9552 = (UTC+05:45) Katmandu 9553 = (UTC+12:00) Auckland, Wellington 9554 = (UTC-03:30) Newfoundland 9555 = (UTC+08:00) Irkutsk 9556 = (UTC+07:00) Krasnoyarsk 9557 = (UTC-04:00) Santiago - old 9558 = (UTC-08:00) Pacific (USA, Canada) 9559 = (UTC-08:00) Tijuana, Baja California (Mexico) 9560 = (UTC+01:00) Brussels, Copenhagen, Madrid, Paris 9561 = (UTC+03:00) Moskow, St. Petersburg, Volgograd 9562 = (UTC-03:00) Buenos Aires, Santiago 9563 = (UTC-05:00) Bogotá, Lima, Quito 9564 = (UTC-04:30) Caracas 9565 = (UTC-11:00) Midway Islands, Samoa 9566 = (UTC+07:00) Bangkok, Hanoi, Jakarta 9567 = (UTC+02:00) Harare, Pretoria 9568 = (UTC+05:30) Sri Jayawardenepura 9569 = (UTC+08:00) Taipeh 9570 = (UTC+10:00) Hobart 9571 = (UTC+09:00) Osaka, Sapporo, Tokyo 9572 = (UTC+13:00) Nuku'alofa 9573 = (UTC-05:00) Indiana (East) 9574 = (UTC-07:00) Arizona 9575 = (UTC+10:00) Vladivostok, Magadan 9576 = (UTC+08:00) Perth 9577 = (UTC+01:00) West.Centr.Africa 9578 = (UTC+01:00) Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna 9579 = (UTC+05:00) Islamabad, Karatschi 9580 = (UTC+10:00) Guam, Port Moresby 9581 = (UTC+09:00) Yakutsk 9582 = (UTC+04:00) Caucasian Standard Time 9583 = (UTC-06:00) Chicago, Dallas, Kansas City, Winnipeg 9584 = (UTC-06:00) Guadalajara, Mexico City, Monterrey - new 9586 = (UTC+04:00) Port Louis 9587 = (UTC-07:00) Chihuahua, La Paz, Mazatlan - new 9588 = (UTC-03:00) Montevideo 9589 = (UTC+05:00) Taschkent 9591 = (UTC-04:00) Georgetown, La Paz, San Juan 9592 = (UTC+08:00) Ulan-Bator 9593 = (UTC-03:00) Cayenne 9594 = (UTC-04:00) Asuncion 9595 = (UTC+12:00) Petropavlovsk-Kamtschatski 9596 = (UTC+03:00) Minsk |  | U32 | ENUM | RW
40005 | Standard/Daylight saving time conversion on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40009 | Operating condition: 235 = Parallel grid operation 381 = Stop |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 798 = Polski 801 = ภาษาไทย |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down: 381 = Stop 1467 = Start 1749 = Full stop |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40029 | Operating status: 235 = Parallel grid operation 381 = Stop 1392 = Fault 1467 = Start 1469 = Shut down 1480 = Waiting for utilities company 1855 = Stand-alone operation 2119 = Derating 16777213 = Information not available |  | U32 | ENUM | RO
40035 | Battery type: 1785 = Lithium-Ion (Li-Ion) |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40073 | Lower discharge limit for int. consumption increase | % | U32 | FIX0 | RW
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 42 = AS4777.3 333 = PPC 438 = VDE0126-1-1 1199 = PPDS 7510 = VDE-AR-N4105 7517 = CEI 0-21 internal 7518 = CEI 0-21 external 7523 = C10/11/2012 7525 = G83/2 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7535 = WorstCase 7536 = Default 7539 = RD1699/413 7549 = AS4777.2_2015 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40149 | Active power setpoint | W | S32 | FIX0 | W
40151 | Eff./reac. pow. contr. via comm.: 802 = Active 803 = Inactive |  | U32 | ENUM | W
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40183 | Phase assignment: 325 = Phase L1 327 = Phase L2 329 = Phase L3 |  | U32 | ENUM | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40187 | Battery nominal capacity | Wh | U32 | FIX0 | RO
40189 | Batt. manuf's max. charge capac. | W | U32 | FIX0 | RO
40191 | Batt. manuf's max. disch. capac. | W | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power 3544 = Linear instantaneous power gradient for over- and underfrequency |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40236 | BMS operating mode: 303 = Off 308 = On 1438 = Automatic 2289 = Charge battery 2290 = Discharge battery 2424 = Presetting |  | U32 | ENUM | W
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1264 = Full dynamic grid support 1265 = Limited dynamic grid support |  | U32 | ENUM | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40262 | No. of charac. pt.s to be used [1] |  | U32 | FIX0 | RW
40264 | No. of charac. pt.s to be used [2] |  | U32 | FIX0 | RW
40266 | No. of charac. pt.s to be used [3] |  | U32 | FIX0 | RW
40282 | X values charact. curve 1 [1] |  | S32 | FIX3 | RW
40284 | X values charact. curve 1 [2] |  | S32 | FIX3 | RW
40286 | X values charact. curve 1 [3] |  | S32 | FIX3 | RW
40288 | X values charact. curve 1 [4] |  | S32 | FIX3 | RW
40290 | X values charact. curve 1 [5] |  | S32 | FIX3 | RW
40292 | X values charact. curve 1 [6] |  | S32 | FIX3 | RW
40294 | X values charact. curve 1 [7] |  | S32 | FIX3 | RW
40296 | X values charact. curve 1 [8] |  | S32 | FIX3 | RW
40306 | Y values charact. curve 1 [1] |  | S32 | FIX3 | RW
40308 | Y values charact. curve 1 [2] |  | S32 | FIX3 | RW
40310 | Y values charact. curve 1 [3] |  | S32 | FIX3 | RW
40312 | Y values charact. curve 1 [4] |  | S32 | FIX3 | RW
40314 | Y values charact. curve 1 [5] |  | S32 | FIX3 | RW
40316 | Y values charact. curve 1 [6] |  | S32 | FIX3 | RW
40318 | Y values charact. curve 1 [7] |  | S32 | FIX3 | RW
40320 | Y values charact. curve 1 [8] |  | S32 | FIX3 | RW
40330 | X values charact. curve 2 [1] |  | S32 | FIX3 | RW
40332 | X values charact. curve 2 [2] |  | S32 | FIX3 | RW
40334 | X values charact. curve 2 [3] |  | S32 | FIX3 | RW
40336 | X values charact. curve 2 [4] |  | S32 | FIX3 | RW
40338 | X values charact. curve 2 [5] |  | S32 | FIX3 | RW
40340 | X values charact. curve 2 [6] |  | S32 | FIX3 | RW
40342 | X values charact. curve 2 [7] |  | S32 | FIX3 | RW
40344 | X values charact. curve 2 [8] |  | S32 | FIX3 | RW
40354 | Y values charact. curve 2 [1] |  | S32 | FIX3 | RW
40356 | Y values charact. curve 2 [2] |  | S32 | FIX3 | RW
40358 | Y values charact. curve 2 [3] |  | S32 | FIX3 | RW
40360 | Y values charact. curve 2 [4] |  | S32 | FIX3 | RW
40362 | Y values charact. curve 2 [5] |  | S32 | FIX3 | RW
40364 | Y values charact. curve 2 [6] |  | S32 | FIX3 | RW
40366 | Y values charact. curve 2 [7] |  | S32 | FIX3 | RW
40368 | Y values charact. curve 2 [8] |  | S32 | FIX3 | RW
40378 | X values charact. curve 3 [1] |  | S32 | FIX3 | RW
40380 | X values charact. curve 3 [2] |  | S32 | FIX3 | RW
40382 | X values charact. curve 3 [3] |  | S32 | FIX3 | RW
40384 | X values charact. curve 3 [4] |  | S32 | FIX3 | RW
40386 | X values charact. curve 3 [5] |  | S32 | FIX3 | RW
40388 | X values charact. curve 3 [6] |  | S32 | FIX3 | RW
40390 | X values charact. curve 3 [7] |  | S32 | FIX3 | RW
40392 | X values charact. curve 3 [8] |  | S32 | FIX3 | RW
40402 | Y values charact. curve 3 [1] |  | S32 | FIX3 | RW
40404 | Y values charact. curve 3 [2] |  | S32 | FIX3 | RW
40406 | Y values charact. curve 3 [3] |  | S32 | FIX3 | RW
40408 | Y values charact. curve 3 [4] |  | S32 | FIX3 | RW
40410 | Y values charact. curve 3 [5] |  | S32 | FIX3 | RW
40412 | Y values charact. curve 3 [6] |  | S32 | FIX3 | RW
40414 | Y values charact. curve 3 [7] |  | S32 | FIX3 | RW
40416 | Y values charact. curve 3 [8] |  | S32 | FIX3 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40480 | Nominal current of all phases | A | U32 | FIX3 | RO
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40631 | Device name |  | STR32 | UTF8 | RW
40719 | Lower lmt deep disch. protect area prior shutdown | % | U32 | FIX0 | RW
40721 | Minimum width of deep discharge protection area | % | U32 | FIX0 | RW
40725 | Area width for conserving battery state of charge | % | U32 | FIX0 | RW
40727 | Minimum width of own consumption area | % | U32 | FIX0 | RW
40729 | Most productive month for battery usage range: 2624 = June profitable 2625 = December profitable |  | U32 | ENUM | RW
40731 | Season operation active: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40789 | Communication version |  | U32 | REV | RO
40791 | Timeout for communication fault indication | s | U32 | FIX0 | RW
40793 | Min. battery charge capac. | W | U32 | FIX0 | W
40795 | Max. battery charge capac. | W | U32 | FIX0 | W
40797 | Min. battery discharge capac. | W | U32 | FIX0 | W
40799 | Max. battery discharge capac. | W | U32 | FIX0 | W
40801 | Mains exch. capac. target value | W | S32 | FIX0 | W
40855 | Down ramp f. charac. act. pt. [1] | % | U32 | FIX1 | RW
40857 | Down ramp f. charac. act. pt. [2] | % | U32 | FIX1 | RW
40859 | Down ramp f. charac. act. pt. [3] | % | U32 | FIX1 | RW
40875 | Up ramp f. charac. act. pt. [1] | % | U32 | FIX1 | RW
40877 | Up ramp f. charac. act. pt. [2] | % | U32 | FIX1 | RW
40879 | Up ramp f. charac. act. pt. [3] | % | U32 | FIX1 | RW
40895 | Adj. time for charac. act. pt. [1] | s | U32 | FIX1 | RW
40897 | Adj. time for charac. act. pt. [2] | s | U32 | FIX1 | RW
40899 | Adj. time for charac. act. pt. [3] | s | U32 | FIX1 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40917 | Characteristic curve number, configuration of characteristic curve mode [1] |  | U32 | FIX0 | RW
40919 | Characteristic curve number, configuration of characteristic curve mode [2] |  | U32 | FIX0 | RW
40921 | Characteristic curve number, configuration of characteristic curve mode [3] |  | U32 | FIX0 | RW
40937 | Activation of the characteristic curve, configuration of characteristic curve mode: [1] 303 = Off 308 = On |  | U32 | ENUM | RW
40939 | Activation of the characteristic curve, configuration of characteristic curve mode: [2] 303 = Off 308 = On |  | U32 | ENUM | RW
40941 | Activation of the characteristic curve, configuration of characteristic curve mode: [3] 303 = Off 308 = On |  | U32 | ENUM | RW
40957 | X-axis ref. characteristic: [1] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40959 | X-axis ref. characteristic: [2] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40961 | X-axis ref. characteristic: [3] 1975 = Voltage in V 1976 = Voltage in percentages of Un 3420 = Hertz 3421 = Hertz as the difference from the nominal frequency 3158 = Active power as a percentage of Pmax |  | U32 | ENUM | RW
40977 | Y-axis ref. characteristic: [1] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) 3678 = Max. power draw in % based on Pmax |  | U32 | ENUM | RW
40979 | Y-axis ref. characteristic: [2] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) 3678 = Max. power draw in % based on Pmax |  | U32 | ENUM | RW
40981 | Y-axis ref. characteristic: [3] 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power 2272 = cos Phi (EEI convention) 3678 = Max. power draw in % based on Pmax |  | U32 | ENUM | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41111 | Voltage monitoring of lower minimum threshold as RMS value | V | U32 | FIX2 | RW
41113 | Voltage monitoring of lower min.threshold as RMS value for tripping time | ms | U32 | FIX0 | RW
41115 | Voltage monitoring of upper maximum threshold as RMS value | V | U32 | FIX2 | RW
41117 | Voltage monitoring of upper max. thresh. as RMS value for tripping time | ms | U32 | FIX0 | RW
41121 | Set country standard: 42 = AS4777.3 333 = PPC 438 = VDE0126-1-1 1199 = PPDS 7510 = VDE-AR-N4105 7517 = CEI 0-21 internal 7518 = CEI 0-21 external 7523 = C10/11/2012 7525 = G83/2 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7535 = WorstCase 7536 = Default 7539 = RD1699/413 7549 = AS4777.2_2015 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41187 | Source of ref. meas. for reactive/active power reduction: 3053 = SMA Energy Meter 3547 = Inverter |  | U32 | ENUM | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
41199 | Set active power limit at grid connection point | % | U32 | FIX0 | RW
41203 | Nominal PV system power | W | U32 | FIX0 | RW
41205 | BMS hardware version |  | U32 | HW | RO
41215 | Fallback power for WCtlCom operating mode | W | S32 | FIX0 | RW
41217 | Set active power limit at grid connection point | W | U32 | FIX0 | RW
41219 | Operating mode for absent reactive power control: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41221 | Timeout for absent reactive power control | s | U32 | Duration | RW
41223 | Fallback react power Q in % of WMax for absent react power ctr | % | S32 | FIX2 | RW
41225 | Operating mode for absent cos Phi spec: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41227 | Timeout for absent cos Phi spec | s | U32 | Duration | RW
41229 | Fallback cos Phi for absent cos Phi spec |  | S32 | FIX4 | RW
41233 | BMS hardware version |  | STR32 | UTF8 | RO
41249 | Begrenzung der Wirkleistungsaufnahme in % | % | S32 | FIX2 | W
41251 | Begrenzung der Leistungsaufnahme in W | W | S32 | FIX0 | W
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW

## STP nn000TL-20, PKG 2.56
SMA Modbus Profile
Modbus register address | Short description / Enumerators | Unit | Format | Type | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Tripower
30053 | Device type: 9098 = STP 5000TL-20 9099 = STP 6000TL-20 9100 = STP 7000TL-20 9102 = STP 9000TL-20 9103 = STP 8000TL-20 9281 = STP 10000TL-20 9282 = STP 11000TL-20 9283 = STP 12000TL-20 |  | U32 | ENUM | RO | Sunny Tripower: STP 5000TL-20 / STP 6000TL-20 / STP 7000TL-20 / STP 8000TL-20 / STP 9000TL-20 / STP 10000TL-20 / STP 12000TL-20 Starting with software package: 2.55.03.R
30057 | Serial number |  | U32 | RAW | RO
30059 | Software package |  | U32 | FW | RO
30197 | Current event number |  | U32 | FIX0 | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains 16777213 = Information not available |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down: 381 = Stop 1467 = Start 1749 = Full stop |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | W
40029 | Operating status: 295 = MPP 381 = Stop 443 = Constant voltage 1392 = Fault 1393 = Waiting for PV voltage 1467 = Start 1469 = Shut down 1480 = Waiting for utilities company 2119 = Derating 16777213 = Information not available |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 560 = EN50438 1013 = Other standard 1020 = Medium-Voltage Directive (Germany) 1199 = PPDS 7501 = RD1663/661-A 7506 = VDE0126-1-1/UTE 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7518 = CEI 0-21 external 7522 = NEN-EN50438 7523 = C10/11/2012 7524 = RD1699 7525 = G83/2 7526 = VFR2013 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7539 = RD1699/413 7549 = AS4777.2_2015 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40244 | Reactive current droop, full dynamic grid support configuration: 1233 = SDLWindV 1020 = Medium-Voltage Directive (Germany) |  | U32 | ENUM | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1265 = Limited dynamic grid support 1264 = Full dynamic grid support |  | U32 | ENUM | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | % | S32 | FIX0 | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40260 | Characteristic curve number of the PV system control procedure P(U) |  | U32 | FIX0 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40809 | Revision status of the logic component |  | U32 | FIX0 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41017 | Adjustment time of characteristic operating point, conf. of grid integr. char. 1 | s | U32 | FIX1 | RW
41019 | Decrease ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41021 | Increase ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41023 | Number of points to be used, conf. of grid integr. char. 1 |  | U32 | FIX0 | RW
41025 | X-axes reference, conf. of grid integration char. 1: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41027 | Y-axes reference, conf. of grid integration char. 1: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power |  | U32 | ENUM | RW
41029 | X value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41031 | Y value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41033 | X value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41035 | Y value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41037 | X value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41039 | Y value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41041 | X value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41043 | Y value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41045 | X value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41047 | Y value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41049 | X value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41051 | Y value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41053 | X value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41055 | Y value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41057 | X value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41059 | Y value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41065 | Adjustment time of char. operating point, conf. of grid integration char. 2 | s | U32 | FIX1 | RW
41067 | Decrease ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41069 | Increase ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41071 | Number of points to be used, conf. of grid integr. char. 2 |  | U32 | FIX0 | RW
41073 | Input unit, conf. of grid integration char. 2: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41075 | Output frequency, conf. of grid integration char. 2: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power |  | U32 | ENUM | RW
41077 | X value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41079 | Y value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41081 | X value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41083 | Y value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41085 | X value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41087 | Y value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41089 | X value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41091 | Y value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41093 | X value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41095 | Y value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41097 | X value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41099 | Y value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41101 | X value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41103 | Y value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41105 | X value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41107 | Y value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41121 | Set country standard: 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 560 = EN50438 1013 = Other standard 1020 = Medium-Voltage Directive (Germany) 1199 = PPDS 7501 = RD1663/661-A 7506 = VDE0126-1-1/UTE 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7518 = CEI 0-21 external 7522 = NEN-EN50438 7523 = C10/11/2012 7524 = RD1699 7525 = G83/2 7526 = VFR2013 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7539 = RD1699/413 7549 = AS4777.2_2015 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41133 | Minimum voltage input [2] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41157 | Start delay input [2] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW

## SBn.n-1AV-40, PKG 1.02
SMA Modbus Profile
Modbus register address | Short description / Enumerators | Unit | Format | Type | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Boy
30053 | Device type: 9319 = Sunny Boy 3.0 9320 = Sunny Boy 3.6 9321 = Sunny Boy 4.0 9322 = Sunny Boy 5.0 |  | U32 | ENUM | RO | Sunny Boy: SB3.0-1AV-40 / SB3.6-1AV-40 / SB4.0-1AV-40 / SB5.0-1AV-40 Starting with software package: 1.02.18.R
30057 | Serial number |  | U32 | RAW | RO
30059 | Software package |  | U32 | FW | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30581 | Grid reference counter reading | Wh | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30823 | Excitation type of cosPhi: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30865 | Power grid reference | W | S32 | FIX0 | RO
30867 | Power grid feed-in | W | S32 | FIX0 | RO
30925 | Connection speed of SMACOM A: 1720 = 10 Mbit/s 1721 = 100 Mbit/s 3581 = No connection speed set |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 1726 = Half duplex 1727 = Full duplex 3582 = No duplex mode set |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31247 | Residual current | A | S32 | FIX3 | RO
34109 | Heat sink temperature | °C | S32 | TEMP | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40003 | Time zone: 9499 = (UTC-AUTO) Automatic via SMA protocol |  | U32 | ENUM | RW
40005 | Standard/Daylight saving time conversion on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 798 = Polski 801 = ภาษาไทย |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down: 381 = Stop 1467 = Start |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl |  | U32 | ENUM | W
40063 | Firmware version of the main processor |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40109 | Country standard set: 27 = Special setting 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 1199 = PPDS 7504 = SI4777-2 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7517 = CEI 0-21 internal 7523 = C10/11/2012 7525 = G83/2 7527 = VFR2014 7528 = G59/3 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7536 = Default 7539 = RD1699/413 7549 = AS4777.2_2015 7550 = NRS97-2-1 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40183 | Phase assignment: 325 = Phase L1 327 = Phase L2 329 = Phase L3 |  | U32 | ENUM | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 2269 = Reactive power charact. curve 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40470 | Island network detect. status: 303 = Off 308 = On |  | U32 | ENUM | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40915 | Set active power limit | W | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41017 | Adjustment time of characteristic operating point, conf. of grid integr. char. 1 | s | U32 | FIX1 | RW
41023 | Number of points to be used, conf. of grid integr. char. 1 |  | U32 | FIX0 | RW
41025 | X-axes reference, conf. of grid integration char. 1: 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41027 | Y-axes reference, conf. of grid integration char. 1: 1977 = Var in percentages of Pmax |  | U32 | ENUM | RW
41029 | X value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41031 | Y value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41033 | X value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41035 | Y value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41037 | X value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41039 | Y value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41041 | X value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41043 | Y value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41061 | 2nd characteristic curve number, configuration of characteristic curve mode |  | U32 | FIX0 | RW
41063 | 2nd activation of the characteristic curve, configuration of characteristic curve mode: 303 = Off 308 = On |  | U32 | ENUM | RW
41065 | Adjustment time of char. operating point, conf. of grid integration char. 2 | s | U32 | FIX1 | RW
41071 | Number of points to be used, conf. of grid integr. char. 2 |  | U32 | FIX0 | RW
41073 | Input unit, conf. of grid integration char. 2: 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41075 | Output frequency, conf. of grid integration char. 2: 1978 = Power in percentages of Pmax |  | U32 | ENUM | RW
41077 | X value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41079 | Y value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41081 | X value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41083 | Y value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41085 | X value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41087 | Y value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41089 | X value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41091 | Y value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41111 | Voltage monitoring of lower minimum threshold as RMS value | V | U32 | FIX2 | RW
41113 | Voltage monitoring of lower min.threshold as RMS value for tripping time | ms | U32 | FIX0 | RW
41115 | Voltage monitoring of upper maximum threshold as RMS value | V | U32 | FIX2 | RW
41117 | Voltage monitoring of upper max. thresh. as RMS value for tripping time | ms | U32 | FIX0 | RW
41121 | Set country standard: |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
41219 | Operating mode for absent reactive power control: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41221 | Timeout for absent reactive power control | s | U32 | Duration | RW
41223 | Fallback react power Q in % of WMax for absent react power ctr | % | S32 | FIX2 | RW
41225 | Operating mode for absent cos Phi spec: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41227 | Timeout for absent cos Phi spec | s | U32 | Duration | RW
41229 | Fallback cos Phi for absent cos Phi spec |  | S32 | FIX4 | RW
41253 | Fast shut-down: 381 = Stop 1467 = Start |  | U32 | ENUM | RW
41255 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | RW
41256 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | RW
41257 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | RW
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW