## Sheet1
ModBus address need set with the RVP 485P remote controller UNI, PRO, FLEX). Meniu: ->Settings->MBaddress
Name | ModBus func. | R/W | Data address DEC | Quantity of data | Description | Value
(0x....) | Coils Read - 01h, Write – 05h, 0Fh ( Present value, Unsigned Word )
Antifrost | 01h_Read_Coils | R | 0 | 1 | Plate heat exchanger frost protection function | 1-active, 0-passive
Fire | 01h_Read_Coils | R | 1 | 1 | Fire alarm | 1-active, 0-passive
Filter | 01h_Read_Coils | R | 2 | 1 | Dirty filter alarm | 1-active, 0-passive
Fan | 01h_Read_Coils | R | 3 | 1 | Fans alarm | 1-active, 0-passive
LowPower | 01h_Read_Coils | R | 5 | 1 | Low voltage | 1-active, 0-passive
Textract | 01h_Read_Coils | R | 6 | 1 | DTJ(100) temperature sensor alarm | 1-active, 0-passive
Texhaust | 01h_Read_Coils | R | 7 | 1 | Exhaust air temperature sensor alarm | 1-active, 0-passive
Tlimit | 01h_Read_Coils | R | 8 | 1 | Supply air temperature sensor alarm | 1-active, 0-passive
RH | 01h_Read_Coils | R | 9 | 1 | DTJ(100) humidity sensor alarm (controller works, in determining the moisture content of 70%) | 1-active, 0-passive
Return Water | 01h_Read_Coils | R | 10 | 1 | Return water temperature sensor alarm | 1-active, 0-passive
ToutDoor | 01h_Read_Coils | R | 11 | 1 | Outside air temperature sensor alarm | 1-active, 0-passive
MotorActive | 01h_Read_Coils | R | 13 | 1 | Fans ON | 1-active, 0-passive
Preheater | 01h_Read_Coils | R | 12 | 1 | Preheater indication | 1-active, 0-passive
Heater | 01h_Read_Coils | R | 14 | 1 | Heater indication | 1-active, 0-passive
(3x....) | Input Read - 04h ( Present value, Unsigned Word ) | R
InDumpper | 04h_Read_Input | R | 14 | 1 | Outside air damper actuator | 0-1
RH_value | 04h_Read_Input | R | 13 | 1 | DTJ(100) humidity sensor value | 0-99
Motor1 | 04h_Read_Input | R | 15 | 1 | Motor1 fan speed value | 0-3
Motor2 | 04h_Read_Input | R | 16 | 1 | Motor1 fan speed value | 0-3
(3x....) | Input Read - 04h ( Present value, Signed Word ) | R
Tlimit | 04h_Read_Input | R | 0 | 1 | Supply air temperature value | Real =(value*10)
Texhaust | 04h_Read_Input | R | 6 | 1 | DTJ(100) temperature sensor value | Real =(value*10)
Textract | 04h_Read_Input | R | 3 | 1 | Exhaust air temperature sensor value | Real =(value*10)
ToutDoor | 04h_Read_Input | R | 9 | 1 | Outside air temperature sensor value | Real =(value*10)
Twater | 04h_Read_Input | R | 12 | 1 | Return water temperature sensor value | Real =(value*10)
(4x....) | Holdings Read – 03h, Write – 06h, 10h ( Present value, Unsigned Word )
Speed | 06h_Write_Holding_Register | R/W | 0 | 1 | Fan speed setting | 0, 1, 2, 3
TsetPoint | 06h_Write_Holding_Register | R/W | 1 | 1 | Supply air temperature set | 0-30
| Report SlaveID – 11h |  |  |  | ( Present value, Unsigned Char )
|  | R |  |  | Eco-200/Ver.706 | ECO706:130412B ( Remote )