## Tabelle1
SMA Modbus Profile
Modbus register address | Short description | Type | Format | Unit | Access
30051 | Device class | U32 | ENUM |  | RO
30053 | Device type | U32 | ENUM |  | RO
30057 | Serial number | U32 | RAW |  | RO
30059 | Software package | U32 | FW |  | RO
30199 | Waiting time until feed-in | U32 | Duration | s | RO
30201 | Condition | U32 | ENUM |  | RO
30203 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
30205 | Nominal power in Warning Mode | U32 | FIX0 | W | RO
30207 | Nominal power in Fault Mode | U32 | FIX0 | W | RO
30211 | Recommended action | U32 | ENUM |  | RO
30213 | Message | U32 | ENUM |  | RO
30215 | Fault correction measure | U32 | ENUM |  | RO
30217 | Grid relay/contactor | U32 | ENUM |  | RO
30219 | Derating | U32 | ENUM |  | RO
30225 | Insulation resistance | U32 | FIX0 | Ohms | RO
30231 | Maximum active power device | U32 | FIX0 | W | RO
30233 | Set active power limit | U32 | FIX0 | W | RO
30247 | Current event number for manufacturer | U32 | FIX0 |  | RO
30513 | Total yield | U64 | FIX0 | Wh | RO
30517 | Daily yield | U64 | FIX0 | Wh | RO
30521 | Operating time | U64 | Duration | s | RO
30525 | Feed-in time | U64 | Duration | s | RO
30529 | Total yield | U32 | FIX0 | Wh | RO
30531 | Total yield | U32 | FIX0 | kWh | RO
30533 | Total yield | U32 | FIX0 | MWh | RO
30535 | Daily yield | U32 | FIX0 | Wh | RO
30537 | Daily yield | U32 | FIX0 | kWh | RO
30539 | Daily yield | U32 | FIX0 | MWh | RO
30541 | Operating time | U32 | Duration | s | RO
30543 | Feed-in time | U32 | Duration | s | RO
30559 | Number of events for user | U32 | FIX0 |  | RO
30561 | Number of events for installer | U32 | FIX0 |  | RO
30563 | Number of events for service | U32 | FIX0 |  | RO
30581 | Grid reference counter reading | U32 | FIX0 | Wh | RO
30583 | Grid feed-in counter reading | U32 | FIX0 | Wh | RO
30599 | Number of grid connections | U32 | FIX0 |  | RO
30769 | DC current input [1] | S32 | FIX3 | A | RO
30771 | DC voltage input [1] | S32 | FIX2 | V | RO
30773 | DC power input [1] | S32 | FIX0 | W | RO
30775 | Power | S32 | FIX0 | W | RO
30777 | Power L1 | S32 | FIX0 | W | RO
30779 | Power L2 | S32 | FIX0 | W | RO
30781 | Power L3 | S32 | FIX0 | W | RO
30783 | Grid voltage phase L1 | U32 | FIX2 | V | RO
30785 | Grid voltage phase L2 | U32 | FIX2 | V | RO
30787 | Grid voltage phase L3 | U32 | FIX2 | V | RO
30789 | Grid voltage phase L1 against L2 | U32 | FIX2 | V | RO
30791 | Grid voltage phase L2 against L3 | U32 | FIX2 | V | RO
30793 | Grid voltage phase L3 against L1 | U32 | FIX2 | V | RO
30803 | Grid frequency | U32 | FIX2 | Hz | RO
30805 | Reactive power | S32 | FIX0 | VAr | RO
30807 | Reactive power L1 | S32 | FIX0 | VAr | RO
30809 | Reactive power L2 | S32 | FIX0 | VAr | RO
30811 | Reactive power L3 | S32 | FIX0 | VAr | RO
30813 | Apparent power | S32 | FIX0 | VA | RO
30815 | Apparent power L1 | S32 | FIX0 | VA | RO
30817 | Apparent power L2 | S32 | FIX0 | VA | RO
30819 | Apparent power L3 | S32 | FIX0 | VA | RO
30825 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RO
30829 | Reactive power set value as a % | S32 | FIX1 | % | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RO
30833 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RO
30835 | Operating mode of feed-in management | U32 | ENUM |  | RO
30837 | Active power limitation P, active power configuration | U32 | FIX0 | W | RO
30839 | Active power limitation P, active power configuration | U32 | FIX0 | % | RO
30865 | Power grid reference | S32 | FIX0 | W | RO
30867 | Power grid feed-in | S32 | FIX0 | W | RO
30881 | PV mains connection | U32 | ENUM |  | RO
30925 | Connection speed of SMACOM A | U32 | ENUM |  | RO
30927 | Duplex mode of SMACOM A | U32 | ENUM |  | RO
30929 | Speedwire connection status of SMACOM A | U32 | ENUM |  | RO
30949 | Displacement power factor | U32 | FIX3 |  | RO
30953 | Internal temperature | S32 | TEMP | °C | RO
30975 | Intermediate circuit voltage | S32 | FIX2 | V | RO
30977 | Grid current phase L1 | S32 | FIX3 | A | RO
30979 | Grid current phase L2 | S32 | FIX3 | A | RO
30981 | Grid current phase L3 | S32 | FIX3 | A | RO
31017 | Current speedwire IP address | STR32 | UTF8 |  | RO
31025 | Current speedwire subnet mask | STR32 | UTF8 |  | RO
31033 | Current speedwire gateway address | STR32 | UTF8 |  | RO
31041 | Current speedwire DNS server address | STR32 | UTF8 |  | RO
31085 | Nominal power in Ok Mode | U32 | FIX0 | W | RO
31159 | Current spec. reactive power Q | S32 | FIX0 | VAr | RO
34113 | Internal temperature | S32 | TEMP | °C | RO
35377 | Number of events for user | U64 | FIX0 |  | RO
35381 | Number of events for installer | U64 | FIX0 |  | RO
35385 | Number of events for service | U64 | FIX0 |  | RO
40003 | Time zone | U32 | ENUM |  | RW
40005 | Standard/Daylight saving time conversion on | U32 | ENUM |  | RW
40009 | Operating condition | U32 | ENUM |  | RW
40013 | Language of the user interface | U32 | ENUM |  | RW
40063 | Firmware version of the main processor | U32 | FW |  | RO
40067 | Serial number | U32 | RAW |  | RO
40095 | Voltage monitoring upper maximum threshold | U32 | FIX2 | V | RW
40109 | Country standard set | U32 | ENUM |  | RO
40133 | Grid nominal voltage | U32 | FIX0 | V | RW
40135 | Nominal frequency | U32 | FIX2 | Hz | RW
40155 | MAC address | STR32 | UTF8 |  | RO
40157 | Automatic speedwire configureation switched on | U32 | ENUM |  | RW
40159 | Speedwire IP address | STR32 | IP4 |  | RW
40167 | Speedwire subnet mask | STR32 | IP4 |  | RW
40175 | Speedwire gateway address | STR32 | IP4 |  | RW
40183 | Phase assignment | U32 | ENUM |  | RW
40185 | Maximum apparent power device | U32 | FIX0 | VA | RO
40195 | Currently set apparent power limit | U32 | FIX0 | VA | RW
40200 | Operating mode of stat.V stab., stat.V stab. config. | U32 | ENUM |  | RW
40204 | Reactive power set value as a % | S32 | FIX1 | % | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. | S32 | FIX2 |  | RW
40208 | cosPhi excit.type, cosPhi config., direct spec. | U32 | ENUM |  | RW
40210 | Operating mode of feed-in management | U32 | ENUM |  | RW
40212 | Active power limitation P, active power configuration | U32 | FIX0 | W | RW
40214 | Active power limitation P, active power configuration | U32 | FIX0 | % | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f) | U32 | ENUM |  | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | U32 | FIX2 | Hz | RW
40222 | cosPhi at start point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40224 | Excit. type at start point, cosPhi(P) char. conf. | U32 | ENUM |  | RW
40226 | cosPhi at end point, cosPhi(P) char. config. | U32 | FIX2 |  | RW
40228 | Excit. type at end point, cosPhi(P) char. config. | U32 | ENUM |  | RW
40230 | Act. power at start point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40232 | Act. power at end point, cosPhi(P) char. config. | U32 | FIX0 | % | RW
40234 | Active power gradient | U32 | FIX0 | % | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration | U32 | ENUM |  | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | U32 | FIX0 | % | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration | U32 | ENUM | 0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | U32 | FIX0 | % | RW
40428 | Frequency monitoring median maximum threshold | U32 | FIX2 | Hz | RW
40430 | Frq. monitoring median max. threshold trip. time | U32 | FIX0 | ms | RW
40432 | Frequency monitoring lower maximum threshold | U32 | FIX2 | Hz | RW
40434 | Frq. monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40436 | Frequency monitoring upper minimum threshold | U32 | FIX2 | Hz | RW
40438 | Frq. monitoring upper min. threshold trip. time | U32 | FIX0 | ms | RW
40440 | Frequency monitoring median minimum threshold | U32 | FIX2 | Hz | RW
40442 | Frq. monitoring median min. threshold trip. time | U32 | FIX0 | ms | RW
40446 | Voltage monitoring upper max. threshold trip. time | U32 | FIX3 | ms | RW
40448 | Voltage monitoring median maximum threshold | U32 | FIX2 | V | RW
40450 | Voltage monitoring median max. threshold trip.time | U32 | FIX0 | ms | RW
40452 | Voltage monitoring lower maximum threshold | U32 | FIX2 | V | RW
40456 | Voltage monitoring lower max. threshold trip. time | U32 | FIX0 | ms | RW
40458 | Voltage monitoring lower minimum threshold | U32 | FIX2 | V | RW
40462 | Voltage monitoring lower min. threshold trip. time | U32 | FIX0 | ms | RW
40464 | Voltage monitoring of median minimum threshold | U32 | FIX2 | V | RW
40466 | Voltage monitoring median min. threshold trip.time | U32 | FIX0 | ms | RW
40472 | Reference voltage, PV system control | U32 | FIX0 | V | RW
40474 | Reference correction voltage, PV system control | S32 | FIX0 | V | RW
40480 | Nominal current of all phases | U32 | FIX3 | A | RO
40482 | Reactive power gradient | U32 | FIX0 | % | RW
40484 | Activation of active power gradient | U32 | ENUM |  | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | U32 | FIX1 | % | RW
40497 | MAC address | STR32 | UTF8 |  | RO
40513 | Speedwire DNX server address | STR32 | IP4 |  | RW
40631 | Device name | STR32 | UTF8 |  | RW
40789 | Communication version | U32 | REV |  | RO
40791 | Timeout for communication fault indication | U32 | FIX0 | s | RW
40915 | Set active power limit | U32 | FIX0 | W | RW
43090 | Login with Grid Guard-Code | U32 | FIX0 |  | RW